HVAC Guide Specifications

# Multi Indoor Unit, Variable Refrigerant Flow –Y-Series

# Section 15700 – Mechanical HVAC

Size Range:

6 to 30 tons nominal Y

Mitsubishi Model Number:

PUHY-P72T(y)hMU-A (-BS) Y-series (COOL/HEAT model)

PUHY-P96T(Y)hMU-A (-BS) Y-series (COOL/HEAT Model)

PUHY-P120T(Y)hMU-A (-BS) Y-series (COOL/HEAT Model)

PUHY-P144T(Y)shMU-A (-BS) Y-series (COOL/HEAT Model)

PUHY-P168T(Y)shMU-A (-BS) Y-series (COOL/HEAT Model)

PUHY-P192T(Y)shMU-A (-BS) Y-series (COOL/HEAT model)

PUHY-P216T(y)shMU-A (-BS) Y-series (COOL/HEAT Model)

PUHY-P240T(y)shMU-A (-BS) Y-series (COOL/HEAT model)

PUHY-P264T(Y)shMU-A (-BS) Y-series (COOL/HEAT model)

PUHY-P288T(Y)shMU-A (-BS) Y-series (COOL/HEAT model)

PUHY-P312T(Y)shMU-A (-BS) Y-series (COOL/HEAT model)

PUHY-P336T(Y)shMU-A (-BS) Y-series (COOL/HEAT model)

PUHY-P360T(Y)shMU-A (-BS) Y-series (COOL/HEAT model)

## Part 1 – General

  - System Description

The variable capacity, heat pump heat recovery air conditioning system shall be a Mitsubishi Electric CITY MULTI VRFZ (Variable Refrigerant Flow Zoning). The CITY MULTI VRFZ systems shall be the Y-Series (cool/heat) split system heat pump.

The Y-Series system shall consist of PUHY outdoor unit, multiple indoor units (-E models), and M-NET DDC (Direct Digital Controls).  The sum of connected capacity of all indoor air handlers shall range from 50% to 130% of outdoor rated capacity.

  - Quality Assurance

- The units shall be listed by Electrical Laboratories (ETL) and bear the ETL label.

- All wiring shall be in accordance with the National Electrical Code (N.E.C.).

- The units shall be manufactured in a facility registered to ISO 9001 and ISO14001 which is a set of standards applying to environmental protection set by the International Standard Organization (ISO).

- A full charge of R-410A for the condensing unit only shall be provided in the condensing unit.

  - Delivery, Storage and Handling

- Unit shall be stored and handled according to the manufacturer’s recommendation.

## Part 2 – Warranty

  - The units shall be covered by the manufacturer’s limited warranty for a period of one (1) year from date of installation.

If the systems are:

1) designed by a certified CITY MULTI Diamond Designer,

2) installed by a certified CITY MULTI Diamond Dealer, AND

3) verified with a completed commissioning report submitted to Mitsubishi

Electric Service Department,

then the units shall be covered by an extended manufacturer’s limited warranty for a period of five (5) years from date of installation.

In addition the compressor shall have a manufacturer’s limited warranty for a period of six (6) years from date of installation.

If, during this period, any part should fail to function properly due to defects in workmanship or material, it shall be replaced or repaired at the discretion of the manufacturer.

This warranty shall not include labor.

  - Manufacturer shall have a minimum of twenty-five years of HVAC experience in the U.S. market.

  - The CITY MULTI VRFZ system shall be installed by a Mitsubishi authorized CITY MULTI Diamond Dealer with extensive CITY MULTI install and service training. Contractor shall be an authorized CITY MULTI Diamond Dealer prior to bid. The mandatory contractor service and install training should be performed by the manufacturer.

## Part 3 – Products

  - Y-SERIES OUTDOOR UNIT

- General:

The Y-Series PUHY outdoor unit shall be specifically used with CITY MULTI VRFZ components.  The PUHY outdoor units shall be equipped with multiple circuit boards that interface to the M-NET controls system and shall perform all functions necessary for operation.  Each outdoor unit module shall be completely factory assembled, piped, wired and run tested at the factory.

.

  - The model nomenclature and unit requirements are shown below.  All units requiring a factory supplied twinning kit shall be piped together in the field, without the need for equalizing line(s).  If an alternate manufacturer is selected, any additional material, cost, and labor to install additional lines shall be incurred by the contractor.

| Outdoor Unit Model Nomenclature |
| --- |
| 208/230 Volt | Twinning Kit | 460 Volt | Twinning Kit |
| Model Number | Units |  | Model Number | Units |  |
| PUHY-P72THMU | (1) PUHY-P72THMU | None | PUHY-P72YHMU | (1) PUHY-P72YHMU | None |
| PUHY-P96THMU | (1) PUHY-P96THMU | None | PUHY-P96YHMU | (1) PUHY-P96YHMU | None |
| PUHY-P120THMU | (1) PUHY-P120THMU | None | PUHY-P120YHMU | (1) PUHY-P120YHMU | None |
| PUHY-P144TSHMU | (2) PUHY-P72THMU | CMY-Y100VBK | PUHY-P144YSHMU | (2) PUHY-P72YHMU | CMY-Y100VBK |
| PUHY-P168TSHMU | (1) PUHY-P96THMU (1) PUHY-P72THMU | CMY-Y100VBK | PUHY-P168YSHMU | (1) PUHY-P96YHMU (1) PUHY-P72YHMU | CMY-Y100VBK |
| PUHY-P192TSHMU | (2) PUHY-P96THMU | CMY-Y100VBK | PUHY-P192YSHMU | (2) PUHY-P96YHMU | CMY-Y100VBK |
| PUHY-P216TSHMU | (1) PUHY-P96THMU (1) PUHY-P120THMU | CMY-Y100VBK | PUHY-P216YSHMU | (1) PUHY-P96YHMU (1) PUHY-P120YHMU | CMY-Y100VBK |
| PUHY-P240TSHMU | (2) PUHY-P120THMU | CMY-Y100VBK | PUHY-P240YSHMU | (2) PUHY-P120YHMU | CMY-Y100VBK |
| PUHY-P264TSHMU | (2) PUHY-P72THMU (1) PUHY-P120THMU | CMY-Y300VBK2 | PUHY-P264YSHMU | (2) PUHY-P72YHMU (1) PUHY-P120YHMU | CMY-Y300VBK2 |
| PUHY-P288TSHMU | (1) PUHY-P72THMU (1) PUHY-P96YHMU (1) PUHY-P120THMU | CMY-Y300VBK2 | PUHY-P288YSHMU | (1) PUHY-P72YHMU (1) PUHY-P96YHMU (1) PUHY-P120YHMU | CMY-Y300VBK2 |
| PUHY-P312TSHMU | (1) PUHY-P72THMU (2) PUHY-P120THMU | CMY-Y300VBK2 | PUHY-P312YSHMU | (1) PUHY-P72YHMU (2) PUHY-P120YHMU | CMY-Y300VBK2 |
| PUHY-P338TSHMU | (1) PUHY-P96THMU (2) PUHY-P120THMU | CMY-Y300VBK2 | PUHY-P338YSHMU | (1) PUHY-P96YHMU (2) PUHY-P120YHMU | CMY-Y300VBK2 |
| PUHY-P360THMU | (3) PUHY-P120THMU | CMY-Y300VBK2 | PUHY-P360YHMU | (3) PUHY-P120YHMU | CMY-Y300VBK2 |

  - Outdoor unit shall have a sound rating no higher than 60 dB(A) individually or 65 dB(A) twinned.  Units shall have a sound rating no higher than 50 dB(A) individually or 55 dB(A) twinned while in night mode operation.  If an alternate manufacturer is selected, any additional material, cost, and labor to meet published sound levels shall be incurred by the contractor.

  - Outdoor unit shall be able to connect to up to 50 indoor units depending upon model.

  - Both refrigerant lines from the outdoor unit to indoor units shall be insulated.

  - The outdoor unit shall have an accumulator with refrigerant level sensors and controls.

  - The outdoor unit shall have a high pressure safety switch, over-current protection and DC bus protection.

  - The outdoor unit shall have the ability to operate with a maximum height difference of 164 feet (294 feet optional) and have a total refrigerant tubing length of 3280 feet.  The greatest length is not to exceed 541 feet between the outdoor unit and the indoor units without the need for line size changes or traps.

  - The outdoor unit shall be capable of operating in heating mode down to -4(F ambient temperature or cooling mode down to 23(F ambient temperature, without additional low ambient controls.  If an alternate manufacturer is selected, any additional material, cost, and labor to meet low ambient operating condition and performance shall be incurred by the contractor.

  - The outdoor unit shall have a high efficiency oil separator plus additional logic controls to ensure adequate oil volume in the compressor is maintained.

- Unit Cabinet:

  - The casing(s) shall be fabricated of galvanized steel, bonderized and finished. Units cabinets shall be able to withstand 960 hours per ASTM B117 criteria for seacoast protected models (–BS models).

- Fan:

  - Each outdoor unit module shall be furnished with one direct drive, variable speed propeller type fan.

  - The fan motor shall have inherent protection, have permanently lubricated bearings, and be completely variable speed.  The fan shall be factory set for operation under 0 in. WG external static pressure, but capable of normal operation under a maximum of 0,24 in. WG external static pressure via dipswitch.

  - The fan motor shall be mounted for quiet operation.

  - The fan shall be provided with a raised guard to prevent contact with moving parts.

  - The outdoor unit shall have vertical discharge airflow.

- Refrigerant

  - R410A refrigerant shall be required for PUHY-T/Y(S)HMU-A outdoor unit systems.

- Coil:

  - The outdoor coil shall be of nonferrous construction with lanced or corrugated plate fins on copper tubing.

  - The coil fins shall have a factory applied corrosion resistant blue-fin finish.

  - The coil shall be protected with an integral metal guard.

  - Refrigerant flow from the outdoor unit shall be controlled by means of an inverter driven compressor.

  - The outdoor coil shall include 4 circuits with two position valves for each circuit, except for the last stage.

- Compressor:

      - Each outdoor unit module shall be equipped with one inverter driven scroll hermetic compressor.  Non inverter-driven compressors shall not be allowed.

  - A crankcase heater(s) shall be factory mounted on the compressor(s).

  - The outdoor unit compressor shall have an inverter to modulate capacity.  The capacity shall be completely variable with a turndown of 18%-4% of rated capacity, depending upon unit size

  - The compressor shall be equipped with an internal thermal overload.

  - The compressor shall be mounted to avoid the transmission of vibration.

- Electrical:

  - The outdoor unit electrical power shall be 208/230 or 460 volts, 3-phase, 60 hertz.

  - The unit shall be capable of satisfactory operation within voltage limitations of 187-228 volts (208V/60Hz) or 207-253 volts (230V/60Hz) or 414-506V (460V/60Hz).

  - The outdoor unit shall be controlled by integral microprocessors.

  - The control circuit between the indoor units and the outdoor unit shall be 24VDC completed using a 2-conductor, non-polar twisted pair shielded cable to provide total integration of the system.

  - PKFY (wall-mountED) INDOOR UNIT

- General:

The PKFY shall be wall-mounted indoor unit section and shall have a modulating linear expansion device. The PKFY shall be used with the Y-Series outdoor unit. The PKFY shall support individual control using M-NET DDC controllers.

- Indoor Unit

The indoor unit shall be factory assembled, wired and run tested.  Contained within the unit shall be all factory wiring, piping, electronic modulating linear expansion device, control circuit board and fan motor.  The unit shall have a self-diagnostic function, 3-minute time delay mechanism, an auto restart function, and a test run switch.  Indoor unit and refrigerant pipes shall be charged with dehydrated air before shipment from the factory.

- Unit Cabinet:

- The casing shall have a white finish.

- Multi directional drain and refrigerant piping offering four (4) directions for refrigerant piping and two (2) directions for draining shall be standard.

- There shall be a separate back plate which secures the unit firmly to the wall.

- Fan:

- The indoor fan shall be an assembly with one or two line-flow fan(s) direct driven by a single motor.

- The indoor fan shall be statically and dynamically balanced to run on a motor with permanently lubricated bearings.

- A manual adjustable guide vane shall be provided with the ability to change the airflow from side to side (left to right).

- A motorized air sweep louver shall provide an automatic change in airflow by directing the air up and down to provide uniform air distribution.

- Filter:

- Return air shall be filtered by means of an easily removable, washable filter.

- Coil:

- The indoor coil shall be of nonferrous construction with smooth plate fins on copper tubing.

- The tubing shall have inner grooves for high efficiency heat exchange.

- All tube joints shall be brazed with phos-copper or silver alloy.

- The coils shall be pressure tested at the factory.

- A condensate pan and drain shall be provided under the coil.

- Both refrigerant lines to the PKFY indoor units shall be insulated.

- Electrical:

- The unit electrical power shall be 208/230 volts, 1-phase, 60 hertz.

- The system shall be capable of satisfactory operation within voltage limits of 187-228 volts (208V/60Hz) or 207-253 volts (230V/60Hz)

- Controls:

- This unit shall use controls provided by Mitsubishi Electric to perform functions necessary to operate the system.  Please refer to Part 5 of this guide specification for details on controllers and other control options.

  - PLFY-P**NBMU-E (4-WAY CEILING-RECESSED CASSETTE WITH GRILLE) INDOOR UNIT

        - General:

- The PLFY-P**NBMU-E shall be a four-way cassette style indoor unit that recesses into the ceiling with a ceiling grille. The indoor unit shall be factory assembled, wired and run tested.  Contained within the unit shall be all factory wiring, piping, electronic modulating linear expansion device, control circuit board and fan motor.  The unit shall have a self-diagnostic function, 3-minute time delay mechanism, an auto restart function, an emergency operation function, a test run switch, and the ability to adjust airflow patterns for different ceiling heights.  Indoor unit and refrigerant pipes shall be charged with dehydrated air before shipment from the factory.

- Unit Cabinet:

      - The cabinet shall be space-saving ceiling-recessed cassette.

      - The cabinet panel shall have provisions for a field installed filtered outside air intake.

      - Branch ducting shall be allowed from cabinet.

      - Four-way grille shall be fixed to bottom of cabinet allowing two, three or four-way blow.

      - The grille vane angles shall be individually adjustable from the wired remote controller to customize the airflow pattern for the conditioned space

- Fan:

- The indoor fan shall be an assembly with a turbo fan direct driven by a single motor.

- The indoor fan shall be statically and dynamically balanced to run on a motor with permanently lubricated bearings.

- The indoor fan shall consist of five (5) speed settings, Low, Mid1, Mid2, High and Auto.

- The fan shall have a selectable Auto fan setting that will adjust the fan speed based on the difference between controller set-point and space temperature.

- The indoor unit shall have an adjustable air outlet system offering 4-way airflow, 3-way airflow, or 2-way airflow.

- The indoor unit shall have switches that can be set to provide optimum airflow based on ceiling height and number of outlets used.

- The indoor unit vanes shall have 5 fixed positions and a swing feature that shall be capable of automatically swinging the vanes up and down for uniform air distribution.

- The vanes shall have an Auto-Wave selectable option in the heating mode that shall randomly cycle the vanes up and down to evenly heat the space.

- If specified, the grille shall have an optional i-see sensor that will measure room temperature variations and adjust the airflow accordingly to evenly condition the space.

- Filter:

- Return air shall be filtered by means of a long-life washable filter

- Coil:

- The indoor coil shall be of nonferrous construction with smooth plate fins on copper tubing.

- The tubing shall have inner grooves for high efficiency heat exchange.

- All tube joints shall be brazed with phos-copper or silver alloy.

- The coils shall be pressure tested at the factory.

- A condensate pan and drain shall be provided under the coil.

- The unit shall be provided with an integral condensate lift mechanism that will be able to raise drain water 33 inches above the condensate pan.

- Both refrigerant lines to the PLFY indoor units shall be insulated.

- Electrical:

- The unit electrical power shall be 208/230 volts, 1-phase, 60 hertz.

- The system shall be capable of satisfactory operation within voltage limits of 187-228 volts (208V/60Hz) or 207-253 volts (230V/60Hz).

- Controls:

- This unit shall use controls provided by Mitsubishi Electric to perform functions necessary to operate the system.

  - PLFY-P**NCMU-E (4-WAY CEILING-RECESSED CASSETTE WITH GRILLE) INDOOR UNIT

    - General:

      - The PLFY-P**NCMU-E shall be a four-way cassette style indoor unit that recesses into the ceiling with a ceiling grille. The indoor unit shall be factory assembled, wired and run tested.  Contained within the unit shall be all factory wiring, piping, electronic modulating linear expansion device, control circuit board and fan motor.  The unit shall have a self-diagnostic function, 3-minute time delay mechanism, an auto restart function, an emergency operation function and a test run switch.  Indoor unit and refrigerant pipes shall be charged with dehydrated air before shipment from the factory.

- Unit Cabinet:

- The cabinet shall be a compact 22-7/16” wide x 22-7/16” deep so it will fit within a standard 24” square suspended ceiling grid.

- The cabinet panel shall have provisions for a field installed filtered outside air intake.

- Four-way grille shall be fixed to bottom of cabinet allowing two, three or four-way blow.

- Fan:

- The indoor fan shall be an assembly with a turbo fan direct driven by a single motor.

- The indoor fan shall be statically and dynamically balanced to run on a motor with permanently lubricated bearings.

- The indoor fan shall consist of three (3) speeds, Low, Mid, and High.

- The indoor unit shall have an adjustable air outlet system offering 4-way airflow, 3-way airflow, or 2-way airflow.

- The auto air swing vanes shall be capable of automatically swinging up and down for uniform air distribution.

- Filter:

- Return air shall be filtered by means of a long-life washable filter.

- Coil:

- The indoor coil shall be of nonferrous construction with smooth plate fins on copper tubing.

- The tubing shall have inner grooves for high efficiency heat exchange.

- All tube joints shall be brazed with phos-copper or silver alloy.

- The coils shall be pressure tested at the factory.

- A condensate pan and drain shall be provided under the coil.

- The unit shall be provided with an integral condensate lift mechanism that will be able to raise drain water 19-3/4” inches above the condensate pan.

- Both refrigerant lines to the PLFY indoor units shall be insulated.

- Electrical:

- The unit electrical power shall be 208/230 volts, 1-phase, 60 hertz.

- The system shall be capable of satisfactory operation within voltage limits of 187-228 volts (208V/60Hz) or 207-253 volts (230V/60Hz).

- Controls:

- This unit shall use controls provided by Mitsubishi Electric to perform functions necessary to operate the system.

  - PMFY (1-WAY CEILING-RECESSED CASSETTE WITH GRILLE) INDOOR UNIT

  - General:

The PMFY shall be a one-way cassette indoor unit that recesses into the ceiling with a ceiling grille and shall have a modulating linear expansion device. The PMFY shall be used with the Y-Series outdoor unit. The PMFY shall support individual control using M-NET DDC controllers.

- Indoor Unit.

The indoor unit shall be factory assembled, wired and run tested.  Contained within the unit shall be all factory wiring, piping, electronic modulating linear expansion device, control circuit board and fan motor.  The unit shall have a self-diagnostic function, 3-minute time delay mechanism, an auto restart function, an emergency operation function and a test run switch.  Indoor unit and refrigerant pipes shall be charged with dehydrated air before shipment from the factory.

- Unit Cabinet:

- The cabinet shall be space-saving ceiling recessed.

- The cabinet panel shall have provisions for a field installed filtered outside air intake.

- Branch ducting shall be allowed from cabinet.

- The one-way grille shall be fixed to bottom of cabinet allowing for one-way airflow.

- Fan:

- The indoor fan shall be an assembly with one line-flow fan direct driven by a single motor.

- The indoor fan shall be statically and dynamically balanced to run on a motor with permanently lubricated bearings.

- The indoor fan shall consist of four (4) speeds, Low, Mid1, Mid2, and High.

- Filter:

- Return air shall be filtered by means of a long-life washable permanent filter.

- Coil:

- The indoor coil shall be of nonferrous construction with smooth plate fins on copper tubing.

- The tubing shall have inner grooves for high efficiency heat exchange.

- All tube joints shall be brazed with phos-copper or silver alloy.

- The coils shall be pressure tested at the factory.

- A condensate pan and drain shall be provided under the coil.

- The unit shall be provided with an integral condensate lift mechanism able to raise drain water 23 inches above the condensate pan.

- Both refrigerant lines to the PMFY indoor units shall be insulated.

- Electrical:

- The unit electrical power shall be 208/230 volts, 1-phase, 60 hertz.

- The system shall be capable of satisfactory operation within voltage limits of 187-228 volts (208V/60Hz) or 207-253 volts (230V/60Hz).

- Controls:

- This unit shall use controls provided by Mitsubishi Electric to perform functions necessary to operate the system.  Please refer to Part 5 of this guide specification for details on controllers and other control options.

  - PDFY (CEILING-CONCEALED DUCTED) INDOOR UNIT

- General:

The PDFY shall be a ceiling-concealed ducted indoor fan coil design that mounts above the ceiling with a 2-position, field adjustable return and a fixed horizontal discharge supply and shall have a modulating linear expansion device. The PDFY shall be used with the Y-Series outdoor unit. The PDFY shall support individual control using M-NET DDC controllers.

- Indoor Unit.

The indoor unit shall be factory assembled, wired and run tested.  Contained within the unit shall be all factory wiring, piping, electronic modulating linear expansion device, control circuit board and fan motor.  The unit shall have a self-diagnostic function, 3-minute time delay mechanism, and an auto restart function.  Indoor unit and refrigerant pipes shall be charged with dehydrated air before shipment from the factory.

- Unit Cabinet:

- The unit shall be, ceiling-concealed, ducted.

- The cabinet panel shall have provisions for a field installed filtered outside air intake.

- Fan:

- The indoor unit fan shall be an assembly with one or two Sirocco fan(s) direct driven by a single motor.

- The indoor fan shall be statically and dynamically balanced and run on a motor with permanently lubricated bearings.

- The indoor unit shall have a ducted air outlet system and ducted return air system.

- Filter:

- Return air shall be filtered by means of a standard factory installed return air filter.

- Optional return filter box (rear or bottom placement) with high-efficiency filter shall be available for all PDFY indoor units.

- Coil:

- The indoor coil shall be of nonferrous construction with smooth plate fins on copper tubing.

- The tubing shall have inner grooves for high efficiency heat exchange.

- All tube joints shall be brazed with phos-copper or silver alloy.

- The coils shall be pressure tested at the factory.

- A condensate pan and drain shall be provided under the coil.

- The condensate shall be gravity drained from the fan coil.

- Both refrigerant lines to the PDFY indoor units shall be insulated.

- Electrical:

- The unit electrical power shall be 208/230 volts, 1-phase, 60 hertz.

- The system shall be capable of satisfactory operation within voltage limits of 187-228 volts (208V/60Hz) or 207-253 volts (230V/60Hz).

- Controls:

- This unit shall use controls provided by Mitsubishi Electric to perform functions necessary to operate the system.  Please refer to Part 5 of this guide specification for details on controllers and other control options.

  - PEFY-NMSU (LOW PROFILE CEILING-CONCEALED DUCTED) INDOOR UNIT

- General:

The PEFY-NMSU (Low Profile) unit shall be a ceiling-concealed ducted indoor fan coil that mounts above the ceiling with a rear return and a fixed horizontal discharge supply and shall have a modulating linear expansion device. The PEFY-NMSU shall be used with the Y-Series outdoor unit. The PEFY-NMSU shall support individual control using M-NET DDC controllers.   PEFY (Low Profile) models shall have an extremely compact profile (7-7/8”) which requires minimal ceiling space.  PEFY-NMSU  models shall feature external static pressure settings up to 0.20 in. WG. Units shall have the ability to control supplemental heat via connector CN24 and a 12 VDC output.

- Indoor Unit.

The indoor unit shall be factory assembled, wired and run tested.  Contained within the unit shall be all factory wiring, piping, electronic modulating linear expansion device, control circuit board and fan motor.  The unit shall have a self-diagnostic function, 3-minute time delay mechanism, and an auto restart function.  Indoor unit and refrigerant pipes shall be charged with dehydrated air before shipment from the factory.

- Unit Cabinet:

- The cabinet shall be space saving, low profile, ceiling-concealed ducted.

- The cabinet panel shall have provisions for a field installed filtered outside air intake.

- Fan:

- The indoor unit fan shall be an assembly with one Sirocco fan direct driven by a single motor.

- The indoor fan shall be statically and dynamically balanced to run on a motor with permanently lubricated bearings.

- The indoor fan shall consist of three (3) speeds, High, Mid, and Low.

- The indoor unit shall have a ducted air outlet system and ducted return air system.

- Filter:

- Return air shall be filtered by means of a standard factory installed return air filter.

- Coil:

- The indoor coil shall be of nonferrous construction with smooth plate fins on copper tubing.

- The tubing shall have inner grooves for high efficiency heat exchange.

- All tube joints shall be brazed with phos-copper or silver alloy.

- The coils shall be pressure tested at the factory.

- A condensate pan and drain shall be provided under the coil.

- The unit shall be provided with an integral condensate lift mechanism able to raise drain water 21 inches above the condensate pan.

- Both refrigerant lines to the PEFY indoor units shall be insulated.

- Electrical:

- The unit electrical power shall be 208/230 volts, 1 phase, 60 hertz.

- The system shall be capable of satisfactory operation within voltage limits of 187-228 volts (208V/60Hz) or 207-253 volts (230V/60Hz).

- Controls:

- This unit shall use controls provided by Mitsubishi Electric to perform functions necessary to operate the system.  Please refer to Part 5 of this guide specification for details on controllers and other control options.

  - PEFY-NMHU (ALTERNATE HIGH STATIC OPTION), CEILING-CONCEALED DUCTED INDOOR UNIT

- General:

The PEFY-NMHU (Alternate High Static Option) unit shall be a ceiling concealed ducted indoor fan coil that mounts above the ceiling with a fixed rear return and a horizontal discharge supply, and shall have a modulating linear expansion device. The PEFY-NMHU shall be used with the Y-Series outdoor unit. The PEFY-NMLU shall support individual control using M-NET DDC controllers. PEFY-NMHU (Alternate High Static Option) models shall feature external static pressure settings up 0.80 in. WG.  Units shall have the ability to control supplemental heat via connector CN24 and a 12 VDC output.

- Indoor Unit.

The indoor unit shall be factory assembled, wired and run tested.  Contained within the unit shall be all factory wiring, piping, electronic modulating linear expansion device, control circuit board and fan motor.  The unit shall have a self-diagnostic function, 3-minute time delay mechanism, and an auto restart function.  Indoor unit and refrigerant pipes shall be charged with dehydrated air before shipment from the factory.

- Unit Cabinet:

  - The cabinet shall be ceiling-concealed, ducted.

  - The cabinet panel shall have provisions for a field installed filtered outside air intake.

- Fan:

  - The indoor unit fan shall be an assembly with one or two Sirocco fan(s) direct driven by a single motor.

  - The indoor fan shall be statically and dynamically balanced to run on a motor with permanently lubricated bearings.

  - The indoor unit shall have a ducted air outlet system and ducted return air system.

- Filter:

  - Return air shall be filtered by a field-supplied filter.

  - Optional rear return filter box with long-life filter shall available for all PEFY-NMHU-E indoor units.

- Coil:

  - The indoor coil shall be of nonferrous construction with smooth plate fins on copper tubing.

  - The tubing shall have inner grooves for high efficiency heat exchange.

  - All tube joints shall be brazed with phos-copper or silver alloy.

  - The coils shall be pressure tested at the factory.

  - A condensate pan and drain shall be provided under the coil.

  - The condensate shall be gravity drained from the fan coil.

  - Both refrigerant lines to the PEFY indoor units shall be insulated.

- Electrical:

  - The unit electrical power shall be 208/230 volts, 1-phase, 60 hertz, except for the PEFY-P72NMHU-E and PEFY-P86NMHU-E. The PEFY-P72NMHU-E and PEFY-P96NMHU=E shall be 208/230 volts, 3-phase, 60 hertz.

  - The system shall be capable of satisfactory operation within voltage limits of 187-228 volts (208V/60Hz) or 207-253 volts (230V/60Hz).

- Controls:

- This unit shall use controls provided by Mitsubishi Electric to perform functions necessary to operate the system.  Please refer to Part 5 of this guide specification for details on controllers and other control options.

  - PVFY-P-E00A VERTICAL AIR HANDLER

A. General

The PVFY shall be a vertical ducted indoor fan coil design with a fixed bottom return, a fixed vertical discharge supply, and a modulating linear expansion device.  The unit shall have the capability to be mounted in either the vertical or horizontal (left position only) and have the capability to integrate into systems with various types of indoor units connected. The PVFY shall be used with the Y-Series outdoor unit. The PVFY shall support individual control using M-NET DDC controllers. Units shall have the ability to control supplemental heat via connector Cn24 and a 12 VDC output.

- Indoor Unit.

The indoor unit shall be factory assembled, wired and run tested.  Contained within the unit shall be all factory wiring, piping, electronic modulating linear expansion device, control circuit board and fan motor.  The unit shall have a self-diagnostic function, 3-minute time delay mechanism, and an auto restart function.  Indoor unit and refrigerant pipes shall be charged with dehydrated air before shipment from the factory.

- Unit Cabinet:

- The cabinet shall be prepainted, preinsultated, 22 gauge galvanized steel.

- Fan:

- The indoor unit fan shall be an assembly with a single direct drive fan with a high efficiency DC motor.

- The indoor fan shall be statically and dynamically balanced and run on a motor with permanently lubricated bearings.

- The indoor unit shall have a ducted air outlet system and ducted return air system.

- The fan shall have 3-speeds with the capability to operate between 0.3-0.5 In.W.G. selectable.

- Filter:

- The contractor shall provide a field fabricated filter rack.

- Coil:

- The indoor coil shall be of nonferrous construction with smooth plate fins on copper tubing.

- The tubing shall have inner grooves for high efficiency heat exchange.

- All tube joints shall be brazed with phos-copper or silver alloy.

- The coils shall be pressure tested at the factory.

- A condensate pan and drain shall be provided under the coil.

- The condensate shall be gravity drained from the fan coil.

- Both refrigerant lines to the PVFY indoor units shall be insulated.

- Electrical:

- The unit electrical power shall be 208/230 volts, 1-phase, 60 hertz.

- The system shall be capable of satisfactory operation within voltage limits of 187-228 volts (208V/60Hz) or 207-253 volts (230V/60Hz).

- Controls:

- This unit shall use controls provided by Mitsubishi Electric to perform functions necessary to operate the system.  Please refer to Part 5 of this guide specification for details on controllers and other control options.

  - PFFY (FLOOR-STANDING-EXPOSED or FLOOR-STANDING-CONCEALED) INDOOR UNIT

- General:

The PFFY shall consist of a floor-standing indoor section with and have a modulating linear expansion device. The PFFY shall be used with the Y-Series outdoor unit. The PFFY shall support individual control using M-NET DDC controllers.

- Indoor Unit

The indoor unit shall be factory assembled, wired and run tested.  Contained within the unit shall be all factory wiring, piping, electronic modulating linear expansion device, control circuit board and fan motor.  The unit shall have a self-diagnostic function, 3-minute time delay mechanism, an auto restart function, and a test run switch.  Indoor unit and refrigerant pipes shall be charged with dehydrated air before shipment from the factory.

- Unit Cabinet, Exposed:

- The casing shall have a beige Acrylic paint finish.

- Unit Cabinet, Recessed:

- The casing shall have a galvanized sheet metal finish.

- Fan:

- The indoor unit fan shall be an assembly with one or two Sirocco fan(s) direct driven by a single motor.

- The indoor fan shall be statically and dynamically balanced to run on a motor with permanently lubricated bearings.

- The indoor fan shall consist of two (2) speeds, High and Low.

- Filter:

- Return air shall be filtered by means of an easily removable washable filter.

- Coil:

- The indoor coil shall be of nonferrous construction with smooth plate fins on copper tubing.

- The tubing shall have inner grooves for high efficiency heat exchange.

- All tube joints shall be brazed with phos-copper or silver alloy.

- The coils shall be pressure tested at the factory.

- A condensate pan and drain shall be provided under the coil.

- Both refrigerant lines to the PFFY indoor units shall be insulated.

- Electrical:

- The unit electrical power shall be 208/230 volts, 1-phase, 60 hertz.

- The system shall be capable of satisfactory operation within voltage limits of 187-228 volts (208V/60Hz) or 207-253 volts (230V/60Hz).

- Controls:

- This unit shall use controls provided by Mitsubishi Electric to perform functions necessary to operate the system.  Please refer to Part 5 of this guide specification for details on controllers and other control options.

  - PCFY (CEILING-SUSPENDED) INDOOR UNIT

  - General:

The PCFY shall be ceiling-suspended indoor unit section and have a modulating linear expansion device. The PCFY shall be used with the Y-Series outdoor unit. The PCFY shall support individual control using M-NET DDC controllers.  Units shall have the ability to control supplemental heat via connector CN24 and a 12 VDC output.

  - Indoor Unit

The indoor unit shall be factory assembled, wired and run tested.  Contained within the unit shall be all factory wiring, piping, electronic modulating linear expansion device, control circuit board and fan motor.  The unit shall have a self-diagnostic function, 3-minute time delay mechanism, an auto restart function, and a test run switch.  Indoor unit and refrigerant pipes shall be charged with dehydrated air before shipment from the factory.

  - Unit Cabinet:

- The casing shall have a white finish.

  - Fan:

- The indoor unit fan shall be an assembly with two, three, or four Sirocco fan(s) direct driven by a single motor.

- The indoor fan shall be statically and dynamically balanced to run on a motor with permanently lubricated bearings.

- The indoor fan shall consist of four (4) speeds, Low, Mid1, Mid2, and High.

- Filter:

- Return air shall be filtered by means of an easily removable, washable filter.

- Coil:

- The indoor coil shall be of nonferrous construction with smooth plate fins on copper tubing.

- The tubing shall have inner grooves for high efficiency heat exchange.

- All tube joints shall be brazed with phos-copper or silver alloy.

- The coils shall be pressure tested at the factory.

- A condensate pan and drain shall be provided under the coil.

- Both refrigerant lines to the PCFY indoor units shall be insulated.

- Electrical:

- The unit electrical power shall be 208/230 volts, 1 phase, 60 hertz.

- The system shall be capable of satisfactory operation within voltage limits of 187-228 volts (208V/60Hz) or 207-253 volts (230V/60Hz)

- Controls:

- This unit shall use controls provided by Mitsubishi Electric to perform functions necessary to operate the system.  Please refer to Part 5 of this guide specification for details on controllers and other control options.

Part 5 – Controls

  - Overview

- General:

The CITY MULTI Controls Network (CMCN) shall be capable of supporting remote controllers, schedule timers, system controllers, centralized controllers, an integrated web based interface, graphical user workstation, and system integration to Building Management Systems via BACnet® and LonWorks®.

  - Electrical Characteristics

- General:

The CMCN shall operate at 24VDC.  Controller power and communications shall be via a common non-polar communications bus.

- Wiring:

Control wiring shall be installed in a system daisy chain configuration from indoor unit to ME remote controller to indoor unit, to the BC controller (main and subs, if applicable) and to the outdoor unit.  Control wiring to remote controllers shall be run from the indoor unit terminal block to the controller associated with that unit.

Control wiring for schedule timers, system controllers, and centralized controllers shall be installed in a daisy chain configuration from outdoor unit to outdoor unit, to system controllers, to the power supply.

Control wiring for the Deluxe MA, Simple MA, and Wireless MA remote controllers shall be from the remote controller to the first associated indoor unit (TB-15) then to the remaining associated indoor units (TB-15) in a daisy chain configuration...

The AG-150A, G-50A and GB-50A system controller shall be capable of being networked with other AG-150A, G-50A and GB-50A system controllers for web based control.

- Wiring type:

Wiring shall be 2-conductor (16 AWG), twisted shielded pair, stranded wire, as defined by the Design Tool AutoCAD output.

Network wiring shall be CAT-5e with RJ-45 connection.

  - CITY MULTI Controls Network

The CITY MULTI Controls Network (CMCN) consists of remote controllers, schedule timers, system controllers, centralized controllers, and/or integrated web based interface communicating over a high-speed communication bus. The CITY MULTI Controls Network shall support operation monitoring, scheduling, error email distribution, personal browsers, tenant billing, online maintenance support, and integration with Building Management Systems (BMS) using either LonWorks® or BACnet® interfaces. The below figure illustrates a sample CMCN System Configuration.

CMCN System Configuration

  - CMCN: Remote Controllers

- Deluxe MA Remote Controller (PAR-21MAA)

The Deluxe MA Remote Controller (PAR-21MAA) shall be capable of controlling up to 16 indoor units (defined as 1 group). The Deluxe MA Remote Controller shall be approximately 5” x 5” in size and white in color with a light-green LCD display. The PAR-21MAA shall support a selection from multiple languages (Spanish, German, Japanese, Chinese, English, Russian, Italian, or French) for display information.  The Deluxe MA supports temperature display selection of Fahrenheit or Celsius. The Deluxe MA Remote Controller shall control the following grouped operations: On/Off, Operation Mode (cool, heat, dry, and fan), temperature set point, fan speed setting, and airflow direction setting. The Deluxe MA Remote Controller shall support timer settings of on/off/temperature up to 8 times in a day in 1-minute increments. The Deluxe MA Remote Controller shall support an Auto Off timer. The Deluxe MA Remote Controller shall be able to limit the set temperature range from the Deluxe MA.  The room temperature shall be sensed at either the Deluxe MA Remote Controller or the Indoor Unit dependent on the indoor unit dipswitch setting. The Deluxe MA Remote Controller shall display a four-digit error code in the event of system abnormality/error.

The Deluxe MA Remote Controller shall only be used in the same group with other Deluxe MA Remote Controllers (PAR-21MAA), Wireless MA (PAR-FL32MA / PAR-FA32MA), or Simple MA Remote Controllers (PAC-YT51CRB), with up to two remote controllers per group.

The Deluxe MA Remote Controller shall require no addressing. The Deluxe MA Remote Controller shall connect using two-wire, stranded, non-polar control wire to TB15 connection terminal on the indoor unit. The PAR-21MAA shall require cross-over wiring for grouping across indoor units.

| PAR-21MAA (Deluxe MA Remote Controller) |
| --- |
| Item | Description | Operation | Display |
| ON/OFF | Run and stop operation for a single group | Each Group | Each Group |
| Operation Mode | Switches between Cool/Dry/Auto/Fan/Heat. Operation modes vary depending on the air conditioner unit. Auto mode is in the R2-Series only. | Each Group | Each Group |
| Temperature Setting | Sets the temperature for a single group. Range of temperature setting Cool/Dry: 67°F-87°F (57°F-87°F for PEFY/PDFY/PFFY-E) Heat: 63°F-83°F (63°F-83°F for PEFY/PDFY/PFFY-E) Auto: 67°F-83°F (63°F-83°F for PEFY/PDFY/PFFY-E) | Each Group | Each Group |
| Fan Speed Setting | Models with 4 air flow speed settings: Hi/Mid-2/Mid-1/Low Models with 3 air flow speed settings: Hi/Mid/Low Models with 2 air flow speed settings: Hi/Low | Each Group | Each Group |
| Air Flow Direction Setting | Air flow direction angles 100%-80%-60%-40%, Swing, Louver ON/OFF. Air flow direction settings vary depending on the model. | Each Group | Each Group |
| Weekly Scheduler | ON/OFF/Temperature setting can be done up to 8 times one day in the week. The time can be set by the 1-minute interval. | Each Group | Each Group |
| Permit / Prohibit Local Operation | Individually prohibit operation of each local remote control function (Start/Stop, Change operation mode, Set temperature, Reset filter). *1: Centrally Controlled is displayed on the remote controller for prohibited functions. | N/A | Each Group *1 |
| Prohibition / Permission of Specified Mode | Setting via the System Controller, the operation for the following modes is prohibited: Cooling Prohibited: Cool, Dry, Auto Heating Prohibited: Heat, Auto Cooling-Heating Prohibited: Cool, Heat, Dry, Auto | N/A | Each Group |
| Display Indoor Unit Intake Temp | Measures and displays the intake temperature of the indoor unit when the indoor unit is operating. | N/A | Each Group |
| Error | When an error is currently occurring on an air conditioner unit, the afflicted unit and the error code are displayed | N/A | Each Unit |
| Test Run | Operates air conditioner units in test run mode. | Each Group | Each Group |
| Ventilation Equipment | Up to 16 indoor units can be connected to an interlocked system that has one LOSSNAY unit. LOSSNAY items that can be set are “Hi”, “Low”, and “Stop”. Ventilation mode switching is not available. | Each Group | Each Group |
| Set Temperature Range Limit | The range of room temperature setting can be limited by the initial setting. The lowest limit temperature can be made higher than the usual (67°F) in cool/dry mode, while the upper limit temperature lower than the usual (83°F) in heat mode. *Function does not work in auto mode setting | Each Group | Each Group |
| Auto Lock Out Function | Setting/releasing of simplified locking for remote control buttons can be performed. Locking of all buttons Locking of all buttons except ON/OFF button | Each Group | Each Group |

- Simple MA Remote Controller (PAC-YT51CRB)

The Simple MA Remote Controller (PAC-YT51CRB) shall be capable of controlling up to 16 indoor units (defined as 1 group). The Simple MA Remote Controller shall be compact in size, approximately 3” x 5” and have limited user functionality.  The Simple MA supports temperature display selection of Fahrenheit or Celsius.  The Simple MA Remote Controller shall allow the user to change on/off, mode (cool, heat, dry, and fan), temperature setting, and fan speed setting. The Simple MA Remote Controller shall be able to limit the set temperature range from the Simple MA   The room temperature shall be sensed at either the Simple MA Remote Controller or the Indoor Unit dependent on the indoor unit dipswitch setting. The Simple MA Remote Controller shall display a four-digit error code in the event of system abnormality/error.

The Simple MA Remote Controller shall only be used in same group with PAR-21MAA (Deluxe MA Remote Controllers), Wireless MA (PAR-FL32MA-E / PAR-FA32MA-E), or with other PAC-YT51CRB (Simple MA Remote Controllers), with up to two remote controllers per group.

The Simple MA Remote Controller shall require no addressing. The Simple MA Remote Controller shall connect using two-wire, stranded, non-polar control wire to TB15 connection terminal on the indoor unit. The PAC-YT51CRB shall require cross-over wiring for grouping across indoor units.

| PAC-YT51CRB (Simple MA Remote Controller) |
| --- |
| Item | Description | Operation | Display |
| ON/OFF | Run and stop operation for a single group | Each Group | Each Group |
| Operation Mode | Switches between Cool/Dry/Auto/Fan/Heat. Operation modes vary depending on the air conditioner unit. Auto mode is in the R2-Series only. | Each Group | Each Group |
| Temperature Setting | Sets the temperature for a single group. Range of temperature setting Cool/Dry: 67°F-87°F (57°F-87°F for PEFY/PDFY/PFFY-E) Heat: 63°F-83°F (63°F-83°F for PEFY/PDFY/PFFY-E) Auto: 67°F-83°F (63°F-83°F for PEFY/PDFY/PFFY-E) | Each Group | Each Group |
| Fan Speed Setting | Models with 4 air flow speed settings: Hi/Mid-2/Mid-1/Low Models with 3 air flow speed settings: Hi/Mid/Low Models with 2 air flow speed settings: Hi/Low | Each Group | Each Group |
| Air Flow Direction Setting | Not Available | N/A | N/A |
| Timer Operation | Not Available | N/A | N/A |
| Permit / Prohibit Local Operation | Individually prohibit operation of each local remote control function (Start/Stop, Change operation mode, Set temperature, Reset filter). *1: Centrally Controlled is displayed on the remote controller for prohibited functions. | N/A | Each Group *1 |
| Display Indoor Unit Intake Temp | Not Available | N/A | N/A |
| Error | When an error is currently occurring on an air conditioner unit, the afflicted unit and the error code are displayed | N/A | Each Unit |
| Test Run | Operates air conditioner units in test run mode. *2 The display for test run mode will be the same as for normal start/stop (does not display “test run”). | Each Group | Each Group *2 |
| Ventilation Equipment | Up to 16 indoor units can be connected to an interlocked system that has one LOSSNAY unit. LOSSNAY items that can be set are “Hi”, “Low”, and “Stop”. Ventilation mode switching is not available. | Each Group | Each Group |
| Set Temperature Range Limit | The range of room temperature setting can be limited by the initial setting. The lowest limit temperature can be made higher than the usual (67°F) in cool/dry mode, while the upper limit temperature lower than the usual (83°F) in heat mode. *Function does not work in auto mode setting | Each Group | Each Group |

- Wireless MA Remote Controller

The Wireless MA Remote Controller (PAR-FL32MA) used in conjunction with the Wireless MA Remote Controller Receiver (PAR-FA32MA) shall be capable of controlling up to 16 indoor units (defined as 1 group). The Wireless MA Remote Controller is approximately 6” x 2-1/4” and the Wireless MA Remote Controller Receiver is approximately 4-3/4” x 2-3/4”.  The Wireless MA Remote Controller shall have a range of 22 feet.  A single Wireless MA Remote Controller shall be capable of signaling multiple Wireless MA Remote Controller Receivers for control of multiple indoor units.  The Wireless MA Remote Controller and Remote Receiver shall support temperature display selection of Fahrenheit or Celsius. The Wireless MA Remote Controller shall control the following grouped operations: On/Off, Operation Mode (cool, heat, dry, and fan), temperature set point, fan speed setting, and airflow direction setting. The Wireless MA Remote Controller shall support 1 on/off timer setting per day.  The room temperature shall be sensed at either the Wireless MA Remote Controller Receiver or the Indoor Unit dependent on the indoor unit dipswitch setting. The Wireless MA Remote Controller shall display a four-digit error code in the event of system abnormality/error.

The Wireless MA Remote Controller and Receiver shall only be used in the same group with other Wireless MA (PAR-FL32MA / PAR-FA32MA), Deluxe MA Remote Controllers (PAR-21MAA) or Simple MA Remote Controllers (PAC-YT51CRB), with up to two remote controllers per group.

The Wireless MA Remote Controller and Receiver shall require no addressing. The Wireless MA Remote Controller Receiver shall connect using two-wire, stranded, non-polar control wire to TB15 connection terminal on the indoor unit. The Wireless MA Remote Controller Receiver shall require cross-over wiring for grouping across indoor units.

| PAR-FL32MA (Wireless MA Remote Controller) |
| --- |
| Item | Description | Operation | Display |
| ON/OFF | Run and stop operation for a single group | Each Group | Each Group |
| Operation Mode | Switches between Cool/Dry/Auto/Fan/Heat. Operation modes vary depending on the air conditioner unit. Auto mode is in the R2-Series only. | Each Group | Each Group |
| Temperature Setting | Sets the temperature for a single group. Range of temperature setting Cool/Dry: 67°F-87°F (57°F-87°F for PEFY/PDFY/PFFY-E) Heat: 63°F-83°F (63°F-83°F for PEFY/PDFY/PFFY-E) Auto: 67°F-83°F (63°F-83°F for PEFY/PDFY/PFFY-E) | Each Group | Each Group |
| Fan Speed Setting | Models with 4 air flow speed settings: Hi/Mid-2/Mid-1/Low Models with 3 air flow speed settings: Hi/Mid/Low Models with 2 air flow speed settings: Hi/Low | Each Group | Each Group |
| Air Flow Direction Setting | Air flow direction angles 100%-80%-60%-40%, Swing, Louver ON/OFF. Air flow direction settings vary depending on the model. | Each Group | Each Group |
| Timer Operation | One ON/OFF setting can be set for one day. | Each Group | Each Group |
| Permit / Prohibit Local Operation | Individually prohibit operation of each local remote control function (Start/Stop, Change operation mode, Set temperature, Reset filter). *1: Centrally Controlled is displayed on the remote controller for prohibited functions. | N/A | Each Group *1 |
| Display Indoor Unit Intake Temp | Measures the intake temperature of the indoor unit when the indoor unit is operating. | N/A | N/A |
| Error | When an error is currently occurring on an air conditioner unit, the afflicted unit and the error code are displayed | N/A | Each Group |
| Test Run | Operates air conditioner units in test run mode. | Each Group | Each Group |
| Ventilation Equipment | Up to 16 indoor units can be connected to an interlocked system that has one LOSSNAY unit. LOSSNAY items that can be set are “Hi”, “Low”, and “Stop”. Ventilation mode switching is not available. | N/A | N/A |

- ME Remote Controller

The ME Remote Controller (PAR-F27MEA-US) shall be capable of controlling up to 16 indoor units (defined as 1 group) from this compact 5” x 5” (approximate) wall-mounted controller. The ME Remote Controller shall be capable of connecting anywhere on the M-NET communication bus and shall not require being physically located in the same room as the indoor unit(s) under its control.

The ME Remote Controller shall control the following grouped operation for up to sixteen indoor units collectively: On/Off, Operation Mode (cool, heat, dry, and fan), temperature setting, fan speed setting, and airflow direction setting. The ME Remote Controller shall have three timer options: one on/off setting defined for one day, repeated daily timer, and auto-off timer function. The ME Remote Controller shall be able to limit the set temperature range from the ME Remote Controller and via a PC through a licensed G-50A/GB-50A. The room temperature shall be sensed at either the ME Remote Controller or the Indoor Unit dependent on the indoor unit dipswitch setting. The ME Remote Controller shall display a four-digit error code in the event of system abnormality/error.

The ME Remote Controller shall only be used in same group with other ME Remote Controllers with a maximum of two ME Remote Controllers per group.

The ME Remote Controller shall require manual addressing using rotary dial switch to the M-NET communication bus. The ME Remote Controller shall connect using two-wire, stranded, non-polar control wire to TB5 connection terminal on the indoor unit.

| PAR-F27MEA-US (ME Remote Controller) |
| --- |
| Item | Description | Operation | Display |
| ON/OFF | Run and stop operation for a single group | Each Group | Each Group |
| Operation Mode | Switches between Cool/Dry/Auto/Fan/Heat. Operation modes vary depending on the air conditioner unit. Auto mode is in the R2-Series only. | Each Group | Each Group |
| Temperature Setting | Sets the temperature for a single group. Range of temperature setting Cool/Dry: 67°F-87°F (57°F-87°F for PEFY/PDFY/PFFY-E) Heat: 63°F-83°F (63°F-83°F for PEFY/PDFY/PFFY-E) Auto: 67°F-83°F (63°F-83°F for PEFY/PDFY/PFFY-E) | Each Group | Each Group |
| Fan Speed Setting | Models with 4 air flow speed settings: Hi/Mid-2/Mid-1/Low Models with 3 air flow speed settings: Hi/Mid/Low Models with 2 air flow speed settings: Hi/Low | Each Group | Each Group |
| Air Flow Direction Setting | Air flow direction angles 100%-80%-60%-40%, Swing, Louver ON/OFF. Air flow direction settings vary depending on the model. | Each Group | Each Group |
| Weekly Scheduler | ON/OFF/Temperature setting can be done up to 8 times one day in the week. The time can be set by the 1-minute interval. | Each Group | Each Group |
| Permit / Prohibit Local Operation | Individually prohibit operation of each local remote control function (Start/Stop, Change operation mode, Set temperature, Reset filter). *1: Centrally Controlled is displayed on the remote controller for prohibited functions. | N/A | Each Group *1 |
| Displays Indoor Unit Intake Temp | Measures the intake temperature of the indoor unit when the indoor unit is operating. | N/A | Each Group |
| Error | When an error is currently occurring on an air conditioner unit, the afflicted unit and the error code are displayed | N/A | Each Unit |
| Timer Operation | Three timer options: - One Day Timer: ON/OFF setting of one time one day - Daily Timer: ON/OFF setting by the One Day timer can be repeated for every day. - Auto OFF timer: OFF timer can be set in a range from 30 minutes to 4 hours. * Setting of Auto OFF timer automatically activates OFF timer at the next operation. | Each Group | Each Group |
| Test Run | Operates air conditioner units in test run mode. | Each Group | Each Group |
| Ventilation Equipment | Up to 16 indoor units can be connected to an interlocked system that has one LOSSNAY unit. LOSSNAY items that can be set are “Hi”, “Low”, and “Stop”. Ventilation mode switching is not available. | Each Group | Each Group |
| Set Temperature Range Limit | The range of room temperature setting can be limited by the initial setting. The lowest limit temperature can be made higher than the usual (67°F) in cool/dry mode, while the upper limit temperature lower than the usual (83°F) in heat mode. *Function does not work in auto mode setting | Each Group | Each Group |
| Auto Lock Out Function | Setting/releasing of simplified locking for remote control buttons can be performed. Locking of all buttons Locking of all buttons except ON/OFF button | Each Group | Each Group |

  - CMCN: System Controllers

- PAC-YT40ANRA: ON/OFF Controller

The PAC-YT40NARA ON/OFF Controller shall be capable of turning ON/OFF up to sixteen groups of indoor units, for a maximum of 50 indoor units. All of the units, up to 50, shall be turned ON/OFF using the main switch. A LED for each group of indoor units, up to 16 groups, shall indicate if there is a failure within each group by flashing. A main LED shall flash if there is an error on any one of the 16 groups for a maximum of 50 indoor units. A LED shall indicate the ON/OFF status for each group of indoor units.  The PACY-YT40ANRA shall be approximately 5” x 5” in size and shall be powered using either the PAC-SC50KUA Power Supply on TB 7 of the outdoor unit or via the indoor transmission line on TB 3 on the outdoor unit. The ON/FF Controller can output via level signal operation state and error state.

| PAC-YT40ANRA (ON/OFF Controller) |
| --- |
| Item | Description | Operation | Display |
| ON/OFF | Run and stop operation for the air conditioner units | Group or Collective | Group or Collective |
| Operation Mode | Not Available | N/A | N/A |
| Temperature Setting | Not Available | N/A | N/A |
| Fan Speed Setting | Not Available | N/A | N/A |
| Air Flow Direction Setting | Not Available | N/A | N/A |
| Room Temp Display | Not Available | N/A | N/A |
| Error | LED flashes during failure. (The error code can be confirmed by removing the cover.) | N/A | Each Group |
| Schedule Operation | Not Available | N/A | N/A |
| Ventilation Operation (Independent) | Group operation of only LOSSNAY units possible. * Only ON/OFF of group | Each Group | Each Group |
| Ventilation Operation (Interlocked) | The LOSSNAY will run in interlock with the operation of indoor unit. * The fan rate and mode cannot be changed. The LED will turn ON only during operation after interlocking. | Each Group | Each Group |
| External Output | Error Output, Operation Output “ON/OFF” and “error/normal” are output with level signal. * The optional output cable is required | Group or Collective | Group or Collective |
| Connection Position | Central System Transmission Line: Connectable (PAC-SC50KUA or PAC-SC51KUA Power Supply is needed. Indoor/Outdoor Transmission Line: Connectable | N/A | N/A |

- PAC-YT34STA: SCHEDULE TIMER

The Schedule Timer (PAC-YT34STA) shall schedule operation for a maximum of 50 indoor units. The maximum number of indoor units supported per one group shall be 16. The maximum number of groups supported shall be 50. The Schedule Timer shall be used in conjunction with PAR-21MAA (Deluxe MA Remote Controllers), Wireless MA (PAR-FL32MA-E / PAR-FA32MA-E), and/or PAR-F27MEA (ME Remote Controllers).

The Schedule Timer shall support up 9 scheduling patterns with up to 16 operations per pattern. Operations shall include on/off, mode selection (cool, heat), set temperature, and prohibition of remote controller functions (on/off, operation mode change, and set temperature adjustment). Patterns shall be applied to each group of indoor units on a per-day basis. The minimum time interval shall be 5-minutes. The Schedule Timer shall display a four-digit error code in the event of system abnormality/error.

The Schedule Timer shall be manually addressed using rotary dial switch to the M-NET communication bus. The Schedule Timer shall be powered using either the PAC-SC50KUA Power Supply or via the indoor transmission line.

The Schedule Timer can be used in conjunction with G-50A Centralized Controller which has higher priority but requires change in dipswitch setting. The Schedule Timer shall accept level or pulse input signals and shall output level signals for specific functions, as defined in below table.

| PAC-YT34STA (Schedule Timer) |
| --- |
| Item | Description | Operation | Display |
| Unit Control | 50 units/ 50 groups (Maximum 16 units connected in one group) | Group or Collective | Each Group |
| Schedule Control | One week. | Each Group | Each Group |
| Operation | ON/OFF | ON/OFF operations can be carried out collectively or for each group. | Each Group | Each Group |
|  | Timer Reset | The timer setting details can be disabled collectively. | Each Group | Each Group |
| Schedule Function | Setting Details | ON/OFF COOL/HEAT Room temperature setting (67°F to 83°F) Operation prohibit (ON/OFF, operation mode, setting temperature) | Each Group | N/A |
|  | Number of Settings | Number of setting patterns: Ten (no setting + nine patterns) (Operation for a week can be set by selecting one of ten patterns for each day.) Number of operations: Up to 16 operations can be set in one pattern. | Each Group | N/A |
|  | Time Setting Unit | The item can be set in five-minute units. | Each Group | N/A |
| Display | Current time and day | N/A | Each Group |
|  | Error state | N/A | Each Group |
|  | Unit operation state | N/A | N/A |
| External Input | Timer Connection and Emergency Stop Input, etc. | The following can be input with the level signals or pulse signals. Level signal: “Emergency stop input” or “Collective ON/OFF” Pulse signal: “Collective ON/OFF” or “Local remote controller prohibit/permit” One input can be selected from those above. | Each Group | N/A |
| External Output | Error Output, Operation Output | “ON/OFF” and “error/normal” are output with the level signal. * Optional output cable is required. | Each Group | N/A |
| Connection Position | Indoor/outdoor transmission line: Connectable Central system transmission line: Connectable (Optional power supply PAC-SC50KUA or PAC-SC51KUA is needed). | N/A | N/A |

- System Group Controller (PAC-SF44SRA)

The System Centralized Controller (PAC-SF44SRA) shall be capable of controlling a maximum of 50 groups or a maximum of 50 indoor units across multiple CITY MULTI outdoor units. The System Group Controller shall be approximately 5”x 5” in size and shall be powered using either the PAC-SC50KUA or PAC-SC51KUA Power Supply on TB 7 of the outdoor unit or via the indoor transmission line on TB 3 on the outdoor unit. The System Group Controller shall have operation controls which can be applied to an individual indoor unit, a group of indoor units (up to 50 indoor units), or all indoor units (collective batch operation). This control set of operation controls for the System Group Controller shall include on/off, operation mode selection (cool, heat, dry, and fan), and temperature setting. The System Group Controller shall be able to enable or disable operation of local remote controllers.

| PAC-SF44SRA (System Group Controller) |
| --- |
| Item | Description | Operation | Display |
| ON/OFF | Run and stop operation for a single group | Each Group or Collective | Each Group or Collective |
| Operation Mode | Switches between Cool/Dry/Auto/Fan/Heat. (Group of Lossnay unit: automatic ventilation/vent-heat/interchange/normal ventilation) Operation modes vary depending on the air conditioner unit. Auto mode is in the CITY MULTI R2-Series only. | Each Group or Collective | Each Group |
| Temperature Setting | Sets the temperature for a single group. Range of temperature setting: Cool/Dry: 67°F-87°F (57°F-87°F for PEFY/PDFY/PFFY-E) Heat: 63°F-83°F (63°F-83°F for PEFY/PDFY/PFFY-E) Auto: 67°F-83°F (63°F-83°F for PEFY/PDFY/PFFY-E) * Range of temperature setting varies depending on the model. | Each Group or Collective | Each Group |
| Fan Speed Setting | Not Available | N/A | N/A |
| Air Flow Direction Setting | Not Available | N/A | N/A |
| Schedule Operation | Schedule operation is achieved in conjunction with the Schedule Timer (PAC-YT34STA) | Using PAC-YT34STA | Using PAC-YT34STA |
| Manual Operation Permit / Prohibit | The ON/OFF, operation mode, setting temperature and filter sign reset operations using the local remote controllers can be prohibited. * (PROHIBIT) will appear when prohibited. Only ON/OFF and filter reset can be prohibited | Each Group or Collective | Each Group or Collective |
| Specific Mode Operation Prohibit | Setting via the System Controller, the operation for the following modes is prohibited: Cooling Prohibited: Cool, Dry, Auto Heating Prohibited: Heat, Auto Cooling-Heating Prohibited: Cool, Heat, Dry, Auto | Each Group Or Collective | Each Group Or Collective |
| Room Temperature Display | Not Available | N/A | N/A |
| Error | When an error is currently occurring on an air conditioner unit, the afflicted unit and the error code are displayed *1 When an error occurs, the LED flashes. The operation monitor screen shows the abnormal unit by flashing it. The error monitor screen shows the abnormal unit address, error code and source of detection. The error log monitor screen shows the time and date, the abnormal unit address, error code and source of detection | N/A | *1 Each Unit or Collective |
| Test Run | Operates air conditioner units in test run mode. | Each Group | Each Group |
| Ventilation Equipment | This interlocked system settings can be performed by the master system controller. When setting the interlocked system, use the ventilation switch the free plan LOSSNAY settings between “Hi”, “Low” and “Stop”. When setting a group of only free plan LOSSNAY units, you can switch between “Normal ventilation”, “Interchange ventilation” and “Automatic ventilation”. | Each Group | Each Group |

  - Input/Output (IO) Boards

- Digital Input Digital Output (DIDO) Board

The DIDO IO board shall be capable of providing On/Off control for non-Mitsubishi equipment via the AG-150A/G-50A/GB-50A Centralized Controller’s licensed web browser functions and the TG-2000A software.  Each DIDO board shall have two digital inputs and two digital outputs and shall be capable of expanding to a total of six digital inputs and six digital outputs.  Each digital output shall be capable of supporting an independent schedule via the AG-150A/G-50A/GB-50A Centralized Controller’s licensed web browser functions and the TG-2000A software.  Status indication of the On/Off state of the non-Mitsubishi equipment shall be either via the On/Off status of the digital output or by receipt of a digital input to the DIDO board.

The DIDO IO board shall be capable of receiving a digital input for interlock settings with the CITY MULTI indoor units or digital outputs on the DIDO board.  Based on the digital input status the DIDO board shall be capable of setting the following parameter on the indoor unit On/Off, Mode, and Set Temperature to predefined settings.  The DIDO board shall also be capable of interlocking the On/Off state of a digital output on the DIDO board based on a digital input status.

- Analog Input (AI) Board

The AI IO board shall be capable of monitoring temperature or humidity via the AG-150A/G-50A/GB-50A Centralized Controller’s licensed web browser functions and the TG-2000A software.  Each AI board shall have two analog inputs.  Each input shall be capable of receiving a 4/20mA, 0/10 VDC, or 1/5 VDC signal for monitoring temperature or humidity.  The AI board shall be capable of monitoring the temperature or humidity input and shall be capable of displaying graphical trending of the temperature or humidity values via the AG-150A/G-50A/GB-50A Centralized Controller’s licensed web browser functions and the TG-2000A software.  Notification of user adjustable high and low level alarms shall be capable of being emailed to distribution list or outputted via a digital output.

The AI IO board shall be capable of setting the following parameters on the indoor unit On/Off, Mode, and Set Temperature to predefined settings based on the input value of the temperature or humidity.  The AI board shall also be capable of interlocking the On/Off state of a digital output on the input value of the temperature or humidity.

  - Centralized Controller

- G-50A Centralized Controller

The G-50A Centralized Controller shall be capable of controlling a maximum of 50 indoor units across multiple CITY MULTI outdoor units. The G-50A Centralized Controller shall be approximately 5”x12” in size and shall be powered from a Power Supply Unit (PAC-SC50KUA). The G-50A Centralized Controller shall support operation superseding that of the remote controllers, system configuration, daily/weekly scheduling, monitoring of operation status, and malfunction monitoring. The G-50A Centralized Controller shall have five basic operation controls which can be applied to an individual indoor unit, a group of indoor units (up to 50 indoor units), or all indoor units (collective batch operation). This basic control set of operation controls for the G-50A Centralized Controller shall include on/off, operation mode selection (cool, heat, dry, and fan), temperature setting, fan speed setting, and airflow direction setting. Since the G-50A provides centralized control it shall be able to enable or disable operation of local remote controllers. In terms of scheduling, the G-50A Centralized Controller shall allow the user to define both daily and weekly schedules with operations consisting of ON/OFF, mode selection, temperature setting, and permit/prohibit of remote controllers.

| G-50A (Centralized Controller) |
| --- |
| Item | Description | Operation | Display |
| ON/OFF | Run and stop operation for a single group | Each Group or Collective | Each Group or Collective |
| Operation Mode | Switches between Cool/Dry/Auto/Fan/Heat. (Group of Lossnay unit: automatic ventilation/vent-heat/interchange/normal ventilation) Operation modes vary depending on the air conditioner unit. Auto mode is in the CITY MULTI R2-Series only. | Each Group or Collective | Each Group |
| Temperature Setting | Sets the temperature for a single group. Range of temperature setting: Cool/Dry: 67°F-87°F (57°F-87°F for PEFY/PDFY/PFFY-E) Heat: 63°F-83°F (63°F-83°F for PEFY/PDFY/PFFY-E) Auto: 67°F-83°F (63°F-83°F for PEFY/PDFY/PFFY-E) * Range of temperature setting varies depending on the model. | Each Group or Collective | Each Group |
| Fan Speed Setting | Models with 4 air flow speed settings: Hi/Mid-2/Mid-1/Low Models with 3 air flow speed settings: Hi/Mid/Low Models with 2 air flow speed settings: Hi/Low | Each Group or Collective | Each Group |
| Air Flow Direction Setting | Air flow direction angles 100%-80%-60%-40%, Swing, *1. Louver cannot be set. Air flow direction settings vary depending on the model. | *1 Each Group or Collective | Each Group |
| Timer Operation | Start/Stop and Enable/Disable can be set 3 times in one day. For a week’s schedule, store three start/stop patterns and one enable/disable pattern. *2 When the timer is set, “Timer Enabled” is shown on the operation setting screen of the LCD. | Each Group or Collective | *2 Each Group |
| Permit / Prohibit Local Operation | Individually prohibit operation of each local remote control function (Start/Stop, Change operation mode, Set temperature, Reset filter). *3: Centrally Controlled is displayed on the remote controller for prohibited functions. | Each Group or Collective | *3 Each Group |
| Display Indoor Unit Intake Temp | Measures and displays the intake temperature of the indoor unit when the indoor unit is operating. | N/A | Each Group |
| Error | When an error is currently occurring on an air conditioner unit, the afflicted unit and the error code are displayed *4 When an error occurs, the LED flashes. The operation monitor screen shows the abnormal unit by flashing it. The error monitor screen shows the abnormal unit address, error code and source of detection. The error log monitor screen shows the time and date, the abnormal unit address, error code and source of detection | N/A | *4 Each Unit or Collective |
| Test Run | Operates air conditioner units in test run mode. | Each Group | Each Group |
| Ventilation Equipment | This interlocked system settings can be performed by the master system controller. When setting the interlocked system, use the ventilation switch the free plan LOSSNAY settings between “Hi”, “Low” and “Stop”. When setting a group of only free plan LOSSNAY units, you can switch between “Normal ventilation”, “Interchange ventilation” and “Automatic ventilation”. | Each Group | Each Group |
| External Input / Output | By using accessory cables you can set and monitor the following. Input By level: “Batch start/stop”, “Batch emergency stop” By pulse: “batch start/stop”, “Enable/disable remote controller” Output: “start/stop”, “error/Normal” ٭5: Requires the external I/O cables (PAC-YG10HA-E) sold separately. | *5 Collective | *5 Collective |

All G-50A Centralized Controllers shall be equipped with one RJ-45 Ethernet port to support interconnection with a network PC via a closed/direct Local Area Network (LAN).

The G-50A Centralized Controller shall be capable of performing initial settings via the keypad and display on the controller or via a PC using the G-50A Centralized Controller’s initial setting browser.

Optional software functions shall be available so that the building manager can securely log into each G-50A via the PC’s web browser to support operation monitoring, scheduling, error email, personal browser for PCs and MACs, and online maintenance diagnostics. Additional optional software functions of Tenant Billing shall be available but shall require TG-2000 Integrated System software in conjunction with G-50A Centralized Controllers. BACnet® interface shall be available through software operating on a dedicated PC and a G-50A license.  The optional software functions shall require advance purchasing and can only be activated upon receipt of a license number from Mitsubishi Electric HVAC.

- GB-50A Centralized Controller

The GB-50A Centralized Controller shall be capable of controlling via a PC a maximum of 50 indoor units across multiple CITY MULTI outdoor units. A field supplied PC shall be required for the GB-50A Centralized Controller.  The GB-50A Centralized Controller shall be approximately 5”x11” in size and shall be powered from a Power Supply Unit (PAC-SC50KUA). The GB-50A Centralized Controller shall support operation superceding that of the remote controllers, system configuration, daily/weekly/annual scheduling, monitoring of operation status, error email notification, online maintenance tool and malfunction monitoring. The GB-50A Centralized Controller shall have basic operation controls which can be applied to an individual indoor unit, a group of indoor units (up to 50 indoor units), or all indoor units (collective batch operation). This basic control set of operation controls for the GB-50A Centralized Controller shall include on/off, operation mode selection (cool, heat, dry, and fan), temperature setting, fan speed setting, airflow direction setting, error email notification, and online maintenance. Since the GB-50A provides centralized control it shall be able to enable or disable operation of local remote controllers via the PC. In terms of scheduling, the GB-50A Centralized Controller shall allow the user to define daily, weekly, and annual schedules with operations consisting of ON/OFF, mode selection, temperature setting, and permit/prohibit of remote controllers.

| GB-50A (Centralized Controller) |
| --- |
| Item | Description | Operation | Display |
| ON/OFF | Run and stop operation for a single group | Each Group or Collective | Each Group or Collective |
| Operation Mode | Switches between Cool/Dry/Auto/Fan/Heat. (Group of Lossnay unit: automatic ventilation/vent-heat/interchange/normal ventilation) Operation modes vary depending on the air conditioner unit. Auto mode is in the CITY MULTI R2-Series only. | Each Group or Collective | Each Group |
| Temperature Setting | Sets the temperature for a single group. Range of temperature setting: Cool/Dry: 67°F-87°F (57°F-87°F for PEFY/PDFY/PFFY-E) Heat: 63°F-83°F (63°F-83°F for PEFY/PDFY/PFFY-E) Auto: 67°F-83°F (63°F-83°F for PEFY/PDFY/PFFY-E) * Range of temperature setting varies depending on the model. | Each Group or Collective | Each Group |
| Fan Speed Setting | Models with 4 air flow speed settings: Hi/Mid-2/Mid-/Low Models with 3 air flow speed settings: Hi/Mid/Low Models with 2 air flow speed settings: Hi/Low | Each Group or Collective | Each Group |
| Air Flow Direction Setting | Air flow direction angles 100%-80%-60%-40%, Swing, *1. Louver cannot be set. Air flow direction settings vary depending on the model. | *1 Each Group or Collective | Each Group |
| Permit / Prohibit Local Operation | Individually prohibit operation of each local remote control function (Start/Stop, Change operation mode, Set temperature, Reset filter). *2: Centrally Controlled is displayed on the remote controller for prohibited functions. | Each Group or Collective | *2 Each Group |
| Indoor Unit Intake Temp | Measures the intake temperature of the indoor unit when the indoor unit is operating. | N/A | Each Group |
| Error | When an error is currently occurring on an air conditioner unit, the afflicted unit and the error code are displayed *3 When an error occurs, the LED flashes. The operation monitor screen shows the abnormal unit by flashing it. The error monitor screen shows the abnormal unit address, error code and source of detection. The error log monitor screen shows the time and date, the abnormal unit address, error code and source of detection | N/A | *3 Each Unit or Collective |
| Ventilation Equipment | This interlocked system settings can be performed by the master system controller. When setting the interlocked system, use the ventilation switch the free plan LOSSNAY settings between “Hi”, “Low” and “Stop”. When setting a group of only free plan LOSSNAY units, you can switch between “Normal ventilation”, “Interchange ventilation” and “Automatic ventilation”. | Each Group | Each Group |
| External Input / Output | By using accessory cables you can set and monitor the following. Input By level: “Batch start/stop”, “Batch emergency stop” By pulse: “batch start/stop”, “Enable/disable remote controller” Output: “start/stop”, “error/Normal” ٭4: Requires the external I/O cables (PAC-YG10HA-E) sold separately. | *4 Collective | *4 Collective |

*GB-50A needs a PC (field supplied) connected together to monitor and operate the air conditioner system.

Standard software functions shall allow the building manager to securely log into each GB-50A via the PC’s web browser to support operation monitoring, scheduling, error email, and online maintenance diagnostics.  Standard software functions shall not expire.  Additional optional software functions shall be available of personal browser for PCs and MACs, Tenant Billing that requires TG-2000 Integrated System software in conjunction with GB-50A Centralized Controllers. BACnet® interface shall be available through software operating on a dedicated PC and a GB-50A license.  Optional software functions shall require advance purchasing and can only be activated upon receipt of a license number from Mitsubishi Electric HVAC.

- AG-150A Centralized Controller

The AG-150A Centralized Controller shall be capable of controlling a maximum of 50 indoor units across multiple CITY MULTI outdoor units. The AG-150A Centralized Controller shall be approximately 7-1/2”x12” in size and shall be powered from a Power Supply Unit (PAC-SC51KUA). The AG-150A Centralized Controller shall support operation superseding that of the remote controllers, system configuration, daily/weekly scheduling, monitoring of operation status, and malfunction monitoring. The AG-150A Centralized Controller shall have five basic operation controls which can be applied to an individual indoor unit, a group of indoor units (up to 50 indoor units), or all indoor units (collective batch operation). This basic control set of operation controls for the AG-150A Centralized Controller shall include on/off, operation mode selection (cool, heat, dry, and fan), temperature setting, fan speed setting, and airflow direction setting. Since the AG-150A provides centralized control it shall be able to enable or disable operation of local remote controllers. In terms of scheduling, the AG-150A Centralized Controller shall allow the user to define both daily and weekly schedules with operations consisting of ON/OFF, mode selection, temperature setting, vane direction, fan speed, and permit/prohibit of remote controllers.

| AG-150A (Centralized Controller) |
| --- |
| Item | Description | Operation | Display |
| ON/OFF | Run and stop operation for a single group | Each Group or Collective | Each Group or Collective |
| Operation Mode | Switches between Cool/Dry/Auto/Fan/Heat. (Group of Lossnay unit: automatic ventilation/vent-heat/interchange/normal ventilation) Operation modes vary depending on the air conditioner unit. Auto mode is in the CITY MULTI R2-Series only. | Each Group or Collective | Each Group |
| Temperature Setting | Sets the temperature for a single group. Range of temperature setting: Cool/Dry: 67°F-87°F (57°F-87°F for PEFY/PDFY/PFFY-E) Heat: 63°F-83°F (63°F-83°F for PEFY/PDFY/PFFY-E) Auto: 67°F-83°F (63°F-83°F for PEFY/PDFY/PFFY-E) * Range of temperature setting varies depending on the model. | Each Group or Collective | Each Group |
| Fan Speed Setting | Models with 4 air flow speed settings: Hi/Mid-2/Mid-1/Low Models with 3 air flow speed settings: Hi/Mid/Low Models with 2 air flow speed settings: Hi/Low | Each Group or Collective | Each Group |
| Air Flow Direction Setting | Air flow direction angles 100%-80%-60%-40%, Swing, *1. Louver cannot be set. Air flow direction settings vary depending on the model. | *1 Each Group or Collective | Each Group |
| Timer Operation | Start/Stop and Enable/Disable can be set 3 times in one day. For a week’s schedule, store three start/stop patterns and one enable/disable pattern. *2 When the timer is set, “Timer Enabled” is shown on the operation setting screen of the LCD. | Each Group or Collective | *2 Each Group |
| Permit / Prohibit Local Operation | Individually prohibit operation of each local remote control function (Start/Stop, Change operation mode, Set temperature, Reset filter). *3: Centrally Controlled is displayed on the remote controller for prohibited functions. | Each Group or Collective | *3 Each Group |
| Display Indoor Unit Intake Temp | Measures and displays the intake temperature of the indoor unit when the indoor unit is operating. | N/A | Each Group |
| Error | When an error is currently occurring on an air conditioner unit, the afflicted unit and the error code are displayed *4 When an error occurs, the LED flashes. The operation monitor screen shows the abnormal unit by flashing it. The error monitor screen shows the abnormal unit address, error code and source of detection. The error log monitor screen shows the time and date, the abnormal unit address, error code and source of detection | N/A | *4 Each Unit or Collective |
| Test Run | Operates air conditioner units in test run mode. | Each Group | Each Group |
| Ventilation Equipment | This interlocked system settings can be performed by the master system controller. When setting the interlocked system, use the ventilation switch the free plan LOSSNAY settings between “Hi”, “Low” and “Stop”. When setting a group of only free plan LOSSNAY units, you can switch between “Normal ventilation”, “Interchange ventilation” and “Automatic ventilation”. | Each Group | Each Group |
| External Input / Output | By using accessory cables you can set and monitor the following. Input By level: “Batch start/stop”, “Batch emergency stop” By pulse: “batch start/stop”, “Enable/disable remote controller” Output: “start/stop”, “error/Normal” ٭5: Requires the external I/O cables (PAC-YG10HA-E) sold separately. | *5 Collective | *5 Collective |

All AG-150A Centralized Controllers shall be equipped with one RJ-45 Ethernet port to support interconnection with a network PC via a closed/direct Local Area Network (LAN).

The AG-150A Centralized Controller shall be capable of performing initial settings via the 9” high-resolution, backlit, color touch panel on the controller or via a PC using the AG-150A Centralized Controller’s initial setting browser.

Optional software functions shall be available so that the building manager can securely log into each AG-150A via the PC’s web browser to support operation monitoring, scheduling, error email, personal browser for PCs and MACs, and online maintenance diagnostics. Additional optional software functions of Tenant Billing shall be available but shall require TG-2000 Integrated System software in conjunction with AG-150A Centralized Controllers. BACnet® interface shall be available through software operating on a dedicated PC and a AG-150A license.  The optional software functions shall require advance purchasing and can only be activated upon receipt of a license number from Mitsubishi Electric HVAC.

  - Web-based User Interface

Licenses per function, per AG-150A/G-50A/GB-50A shall be required.

All PCs shall be field supplied.

- PC-Monitoring (SW-Mon)

The CMCN shall be capable of monitoring and operating all indoor units from a networked PC’s web browser for up to 50 units per AG-150A/G-50A/GB-50A centralized controller.

- PC Scheduling (SW-Sch)

The CMCN shall be capable of creating customized daily, weekly, and annual schedules from a network PC’s web browser for up to 50 units per AG-150A/G-50A/GB-50A.  Schedules shall be applied to a single indoor unit, a group of indoor units, or collectively (batch) to all indoor units controlled by the AG-150A/G-50A/GB-50A.

- Online Error Email (SW-Email)

The CMCN shall be capable of sending detailed alerts to customizable distribution lists based on user defined error types.

- Personal Web Browser (SW-Pweb)

The CMCN shall be capable of allowing up to 50 individual users to monitor and control user defined zones via a network PC or MAC’s web browser.

- Online Maintenance Diagnostics (SW-Maint)

The CMCN shall be capable of performing maintenance diagnostics via a network PC and AG-150A/G-50A/GB-50A centralized controller using Maintenance Tool Software.

- Tenant Billing (SW-Charge)

The CMCN shall be capable of calculating CITY MULTI energy usage in kWh and in a monetary amount based on the energy consumption of the outdoor unit(s) divided among the associated indoor units.  This software is used in conjunction with the TG-2000 software a networked PC, and Watt Hour Meters (WHM).

  - Graphical User Workstation Software

The Graphical User Workstation Software (TG-2000) shall require a field supplied PC.

- TG-2000 Software

The TG-2000 Integrated System Software shall enable the user to control multiple AG-150A/G-50A/GB-50As and shall provide additional functions such as tenant billing from a single, dedicated network PC configured with the TG-2000 software. The TG-2000 configured computer shall be capable of controlling up to forty AG-150A/G-50A/GB-50A Centralized Controllers with a maximum of 2,000 indoor units across multiple CITY MULTI outdoor units. The TG-2000 software shall be required if the user wants to simultaneously control more than 1 AG-150A/G-50A/GB-50A Centralized Controllers from a single PC using a single software session. Licensing per function, per AG-150A/G-50A/GB-50A Centralized Controller shall be required for the TG-2000 software.  Optional software features shall be available through the TG-2000 software including tenant billing. These optional software features shall require the TG-2000 software, advance purchase from the customer, and licensing from Mitsubishi to enable feature activation.

| TG-2000 (Integrated System Software) |
| --- |
|  | AG-150A/ G-50A/GB-50A License |
| Item | Details | PC Monitoring | PC Scheduling | Tenant Billing |
| ON/OFF | The units can turn ON and OFF for all floors or in a block, floor, or group of units. | √ |  |  |
| Operation Modes | The operation mode can be switched between COOL, DRY, FAN, AUTO, and HEAT for all floors or in a block, floor, or group of units | √ |  |  |
| Temperature Setting | The room temperature can be set for all floors in a block, floor, or group of units. Set temperature range Cool/Dry: 67°F-83°F Heat: 67°F-83°F Auto: 67°F-83°F * Depends on unit type | √ |  |  |
| Fan Speed | The fan speed can be set to four stages for all floors or in a bloc, floor, or group of units | √ |  |  |
| Air Direction | The air direction can be set in four vertical directions or to swing for all floors or in block, floor, or group of units. (The selectable air direction differs according to the model.) | √ |  |  |
| Interlocked Unit ON/OFF LOSSNAY | If there is an interlocked unit (LOSSNAY), then the unit can be turned ON (strong/weak) or OFF for all floors or in a block, floor, or group of units. (Note that the ventilation mode cannot be selected for interlocked units.) | √ |  |  |
| Local Operation Prohibit | The items for which operation with the local remote controller are to be prohibited can be selected for all floors or in a block, floor, or group of units. (The items that can be prohibited are ON/OFF, operation mode, set temperature and filter sign reset.) | √ |  |  |
| Annual / Weekly Schedule | The annual/weekly schedule function can be used by registering the license. Two settings, such as seasonal settings for summer and winter, can be saved. | √ | √ |  |
| Power Rate Apportionment Charging | An RS-485 watt-hour meter (WHM) is connected to calculate the air conditioning charges based on the amount each tenant’s air-conditioner has operated. Two charging rates can be applied per day. | √ |  | √ |
| History | Up to 3,000 items for the error history and up to 10,000 items for operation history can be saved. Each history file can be output as a daily report or monthly report in CSV format. (The operation history consists only of the operations carried out with the TG-2000 and is limited to some limited operation items.) | √ |  |  |
| Operation Time Monitor | The cumulative operation time of each indoor unit can be viewed or output as a CSV format file. (This function is valid only when the charging function license is registered.) | √ |  | √ |
| Filter Sign Display Mask | The filter sign display at the remote controllers can be disabled. | √ |  |  |
| Night Set-Back Function *1, *4 | Heating from 55°F and higher can be set using the schedule. | √ |  |  |
| Set Temperature Limit *1 | The set temperature lower limit can be set for cooling and the upper limit for heating. (ME remote controller required) | √ |  |  |

*1: Compatible with TG-2000 Ver. 4.10 or later, G-50A Ver. 2.51 or later

*2: Compatible with TG-2000 Ver. 4.30 or later, G-50A Ver. 2.51 or later

*3: Compatible with TG-2000 Ver. 4.60 or later, G-50A Ver. 2.70 or later

*4: With Night Set-Back function, the CITY MULTI system can run at heating mode with target temperature set to 55ºF under schedule control. This function can protect the room from dropping down to extremely low temperature in the evenings.

  - CMCN: System Integration

The CMCN shall be capable of supporting integration with Building Management Systems (BMS) via our LonWorks® and BACnet® interfaces.

- LMAP03U: LonWorks® Interface

The Mitsubishi Electric HVAC LonWorks®  interface, LMAP03U, shall support up to fifty indoor units with a variety of network variables on a per indoor unit basis. Input variables include, but are not limited to, on/off, operation mode, fan speed, prohibit remote controller, and filter sign reset. Output variables include, but are not limited to, model size, alarm state, error code, and error address.

- PAC-YTG31CDA: BACnet® Interface

The Mitsubishi Electric HVAC BACnet® interface, PAC-YG31CDA (SW-BACnet), shall be compliant with BACnet®/IP (ANSI/ASHRAE 135-1995, 135a) and UDP/IP of Ethernet (ANSI/ASHRAE 135-1995, 135b). The BACnet® interface shall require a dedicated network computer and activated BACnet® software function via Mitsubishi Electric HVAC issued license. The BACnet® software license shall be on a per AG-150A/G-50A/GB-50A basis for a maximum of 50 indoor units controlled by one AG-150A/G-50A/GB-50A Centralized Controller. The BACnet® interface shall support a maximum of ten AG-150A/G-50A/GB-50A Centralized Controllers for a maximum of 500 indoor units.  Operation and monitoring points include, but are not limited to, on/off, operation mode, fan speed, prohibit remote controller, filter sign reset, alarm state, error code, and error address.

  - Power Supply (PAC-SC50KUA)

The power supply shall supply 12VDC (TB 3) for the G-50 centralized controller and 24VDC (TB 2) voltage for the central control transmission.

  - Power Supply (PAC-SC51KUA)

The power supply shall supply 24VDC (TB 3) for the AG-150 centralized controller and 24VDC (TB 2) voltage for the central control transmission.

  - Mr. Slim M-Series and P-Series Control

- The CMCN shall have the capability of controlling and monitoring the Mitsubishi Electric Mr. Slim MSY and MSZ units through the use of an adaptor to allow the MSY and MSZ units to communication on the M-Net communication bus.

- The CMCN shall have the capability of controlling and monitoring the Mitsubishi Electric Mr. Slim PUY and PUZ units through the use of an adaptor to allow the PUY and PUZ units to communication on the M-Net communication bus.