Guide Specifications

Split System Cooling Outdoor Units – 13 SEER, 1 to 5 Tons:  CZB SERIES

General:

This guide specification is for split system condensing units that are part of a light commercial split system air conditioning application using R-410. These units are manufactured by York Unitary Products Group, in an ISO 9001 certified facility. The condensing units must be certified in accordance with the Unitary Small Equipment certification program, under ARI Standard 210/240, and are designed to be part of a custom matched system. Condensing units color shall match the building color.

Unit shall have 5 years parts and labor warranty and 10 years compressor parts warranty.

Description:

The outdoor unit must be a single stage heat pump product, which meets 13 SEER minimum efficiency as rated in a matched system under the ARI certification program.  The design shall provide for easy access to the electrical compartment and compressor, and be factory wired and tested.  Top discharge is required to direct exhausted air away from the structure or surrounding landscaping.  Operating sounds are to be minimized by using upward discharge, cushioned compressor mounts, and rigid top panel to isolate motor sounds/ vibration.

Unit Cabinet – Outdoor unit cabinets shall be made of durable construction materials, using pre-painted galvanized steel which provides a paint-to-steel bond that resists corrosion and rust creep. Special primers and paint should be used to reduce paint fading from sunlight exposure. All internal coil sheet metal parts shall be made of G90 pre-painted steel.   The base pan shall be a formed unit, constructed of 18 gauge, G90 galvanized steel. The condenser coil shall be equipped with a coil guard of polypropylene mesh and a wire guard to protect the fin structure.

Outdoor (Condenser) Fan Assembly - Fan shall be a direct drive blower assembly, with a single speed PSC motor and a propeller type fan assembly. Bearings shall be permanently lubricated for longer life and low maintenance.  The motor wiring shall be connected within the control box for ease of service.

Refrigerant Components - Outdoor coils shall have aluminum plate fins that are mechanically bonded to seamless, internally enhanced copper tubes with all joints brazed. These shall be direct expansion, draw-through design style coils.   The unit must include a bi-flow filter-dryer on the liquid line. Refrigerant connections must be sweat fit, include re-usable brass service valves for both liquid line and vapor line and be fully exposed for installation and service access. The unit shall have hi and low pressure switch.

Compressors - Compressors shall be hermetic type, direct drive, internally protected with high pressure relief and over temperature sensors.  The hermetic motor shall be suction gas cooled and have a voltage range of +/- 10% of the unit nameplate voltage.  Internal spring isolation and sound muffling is required to minimize vibration and operating noise.  The compressors shall be externally isolated as well using independent mounting methods. Hard start kits shall be available for non-scroll compressor applications when required.

Isolated Compressor Compartment.

For noise reduction, provide an insulated compressor compartment with service access.

Provide low speed condenser fans for low sound level.

Provide and install a T-2950 365 day’s time o’clock thermostat with digital read out.

ArmorGuard SS316 Coils and Casing Coating:

Condenser and Evaporator coils must be treated with ArmorGuard SS316, water reducible, liquid stainless steel hard acrylic emulsion corrosion protection coating with 316 stainless steel flake. Coating must be non flammable, non hazardous, environmentally safe, super low VOC, and offer high corrosion protection with superior adhesion and proven long term durability. Coating to be UV resistant and USDA approved.

Low Ambient Application in Cooling Mode

Provide low ambient fan cycling controller to allow cooling down to 0 F