Guide Specifications

Split System Cooling Only Condensing Units Models: YC090-240, YD120-240

General

• Factory assembled, single piece, air cooled condensing unit designed for outdoor installation.

• Factory wired, piped, and tested for leakage and functionality to assure trouble-free installation and startup.

• Rated in accordance with ARI Standard 340/360.

• Manufactured in a facility registered under the ISO 9002 manufacturing quality standard.

• Designed and tested in accordance with ASHRAE 15 Safety Code for Mechanical Refrigeration and comply with

NEC.

• Cooling performance rated in accordance with DOE and ARI test procedures.

• CSA listed and classified to UL 1995/CAN/CSA No. 236- M90 standards.

• One year limited parts warranty on complete unit with an additional four year compressor warranty.

Unit Operating Characteristics

Operating Range shall be between 125° F to 40° F in cooling as standard from factory.

• The capacity of the condensing unit shall meet or exceed _____ Btuh at a suction temperature of _____ F. The

power consumption at full load shall not exceed _____ kW.

• The combination of the condensing unit and the evaporator or fan coil unit shall have a total net cooling capacity of

_____ Btuh or greater at conditions of _____ cfm entering-air temperature at the evaporator at _____ F wet bulb

and _____ F dry bulb, and air entering the condensing unit at _____F.

• The system shall have an EER of _____ Btuh/ Watt or greater at standard ARI conditions.

Installer Shall

• Furnish York® air-cooled condensing units or equivalent in accordance with the performance schedule shown on the plans

• Unit shall be stored and handled in accordance with unit manufacturer's instructions.

• Install each unit as shown on the plans in accordance with the manufacturer’s recommendations and all applicable

national and local codes

Unit Construction

• Constructed of zinc-coated, galvanized steel.

• Exterior surfaces bonded and coated with baked enamel finish by a powder paint process capable of withstanding a minimum of 1000 salt spray hours according to ASTM B117.

• Cabinet screws that comply with ASTM B117 salt spray test for a minimum of 750 hours.

• Permanently attached heavy-gage perimeter base rails with forklift slots and lifting holes.

• Removable access panels to all internal components.

• Separate access panel to controls.

• Access panels to allow outdoor coil cleaning.

Compressor(s)

• Hermetic scroll type internally protected with high pressure relief and over temperature protection.

• Two stage units operate in 50% capacity increments.

• Suction gas cooled

• Voltage range of ±10% of unit nameplate voltage.

• Neoprene isolators minimize sound transmission and vibration.

• Belly-band crankcase heaters keep refrigerant from diluting sump oil.

• Full charge of compressor oil

Outdoor Condenser Unit Coils

• Draw thru configuration

• Constructed with Micro-channel aluminum fins and aluminum tubing. All refrigerant tubing must share a common

header.

Condenser Fans

• Direct driven propeller-type fans

• Statically and dynamically balanced

• Aluminum blades riveted to corrosion resistant steel spider brackets.

• Arranged for vertical air discharge.

• Equipped with PVC coated steel wire safety guards.

Condenser Motors

• Totally enclosed, air over cooled.

• Inherent overload protection.

• Permanently lubricated bearings.

• Must cycle to allow cooling operation down to 40°F.

Refrigerant Piping

• Solid core filter-drier(s) ship loose for field installation.

• Liquid and suction line service valves with gauge ports.

• Suction and discharge line service ports accessible from unit. Ports capped for leak prevention.

• Liquid line magnetic check valves

• Holding charge of R410A refrigerant.

Electrical Requirements

• Single-point connection electrical power.

• Nominal unit electrical characteristics shall be _____ v, 3-ph, 60 Hz. The unit shall be capable of satisfactory

operation within voltage limits of ____ v to _____ v.

• Condenser fan motors and secondary of transformers shall be grounded.

Unit Controls

• All 24-volt control circuit, powered by a 24 volt transformer(s) and protected by a resettable breaker.

• Conventional thermostat must provide operation for condensing units without an “O” output from the thermostat.

• Low voltage terminal strip for simple hook-up.

• Compressor motor protection shuts down unit for motor over-current, over-temperature or low voltage conditions.

• Safety lockouts provide reset capability at the space thermostat or base unit should any of the following standard

safety devices trip and shut off compressor:

a. Loss-of-charge/Low-pressure switch.

b. High-pressure switch.

c. Control board diagnostics and fault code display.

d. Safety lockouts send a 24 volt signal to the control board's "X" terminal, allowing notification to the user

via the thermostat fault light (if present).

e. Control board shall retain last 5 fault codes in nonvolatile memory, which will not be lost in the event of a

power loss. An LED (light-emitting diode) indicator flashes a fault code that indicates which safety switch

has tripped.

Non-fused Disconnect Switch

• Factory-installed, internally mounted.

• Accessible from outside the unit.

• NEC and UL approved non-fused switch.

• Provides power off lockout capability.

Convenience Outlet

• Factory-installed, internally mounted.

• Accessible from outside the unit.

• 115V, 15 amp GFI receptacle with independent fuse protection.

• Required voltage provided by factory-installed step down transformer or field supplied 115v circuit.

Low-ambient Head Pressure Control

• Standard operation down to 40 °F without a low ambient kit.

• Operation down to 0°F with a field-installed low ambient kit accessory. The controller modulates the fan motor

speed in response to liquid line temperature or pressure.

Coil Guard

Factory or field installed decorative grille shall be placed on the units to protect condenser coil after installation.

Hail Guard Package

Field installed hail guard package shall protect coils against damage from hail and other flying debris.

Phenolic Coated Condenser Coils

Special phenolic coating available as a factory option on both outdoor and indoor coils.

Each Unit Shall Be:

• Covered by a 1-year limited parts warranty on the complete unit and 5-year on compressor(s).

• In current production with published literature available to check performance, limitations, specifications, power requirements, dimensions, operation and appearance.

• Indoor unit shall be equipped with a V-belt drive option that will permit the blower RPM to be adjusted to meet the CFM requirements of the air delivery system. (Refer to Technical Guide for Airflow Capabilities.)

Each Unit Enclosure Shall Have:

• Exterior panels of 18 gauge steel, finished with baked enamel to provide a long lasting quality appearance

• Removable panels to provide easy access to the internal components for maintenance and service on condensing units and air handlers

• Air handling units must have a filter rack that accepts both 2” and 4” filters.

• The dimensions of each unit shall not exceed those specified in the manufacture’s literature.

• The minimum application clearances for condensing units and air handlers must meet those specified in the manufacturer’s literature.

The Blower Motor Shall:

• Be mounted within the insulated cabinet to minimize the transmission of sound to the surrounding space, and any motor 7.5 HP or greater must have a service factor of 1.15.

The Evaporator Coil Shall:

• Consist of copper tubes arranged in staggered rows, mechanically expanded into aluminum fins

• Be draw-through

• Include factory-mounted distributors, expansion valves and solenoid valves for capacity reduction.

The Blower Wheels Shall:

Be dynamically balanced to minimize the levels of sound and vibration generated by the unit.