YORK® MECHANICAL SPECIFICATIONS

SINGLE PACKAGE GAS/ELECTRIC ROOFTOP UNIT

2 THRU 5 NOMINAL TONS

AFFINITY™ SERIES

Size Range:	2 to 5 Tons Nominal Cooling

36,000 to 110,000 BTUH Nominal Gas Heating Output

Model Series:	DNX, DNY and DNZ

GENERAL

Units shall be manufactured by York International Unitary Products Group in an ISO 9001 certified facility. YORK’s Affinity™ package units give you the flexibility and choices you need in today’s market. These packaged cooling/heating air conditioners are designed for outdoor installation. Only utility and duct connections are required at the point of installation. The single or two stage gas fired heaters have aluminized steel tubular heat exchangers and spark to pilot ignition. They are available in natural gas with field conversion to propane.

DESCRIPTION

Units shall be factory-assembled, single packaged, Electric Cooling/Gas Heating units, designed for outdoor mounted installation. For SEER ratings, refer to technical literature. They shall have built in, equal size, field convertible duct connections for down discharge supply/return or horizontal discharge supply/return. The units shall be factory wired, piped, charged with R-410A Refrigerant and factory tested prior to shipment. All unit wiring shall be both numbered and color coded. All units shall be manufactured in a facility certified to ISO 9001 standards, and the cooling performance shall be rated in accordance with DOE and ARI test procedures. The heating performance shall be rated to DOE and GAMA test procedures. Units shall be CSA listed and classified to ANSI Z21.47/CAN/CSA 2.3 standards and UL 1995/CAN/CSA No. 236-M90 conditions.

UNIT CABINET

Unit cabinet shall be constructed of G90 galvanized steel, with exterior surfaces coated with a non-chalking, powdered paint finish, certified at 1000 hours salt spray test per ASTM-B117 standards. The unit top shall be a single piece “Water Shed” design, with drip edges and no-seam corners to provide optimum water integrity. Unit shall have a rigidly mounted condenser coil guard to provide protection from objects and personnel after installation. Indoor blower section shall be insulated with up to 3/4” thick, aluminum, foil faced insulation, fastened to prevent insulation from entering the air stream. Cabinet panels shall be “large” size, easily removable for servicing and maintenance, with built-in lift handles. Unit shall be built on a formed, “Super-Structure” design base pan, with embossments at critical points to add strength, rigidity and aid in minimizing sound. Full perimeter base rails shall be provided to assure reliable transit of equipment, overhead rigging, for truck access and proper sealing on roof curb applications. Base rails shall be removable, when required, to lower unit height. Filters shall be furnished and be accessible through a removable access door, sealed airtight. Units vertical discharge and return duct configuration shall be designed to fit between standard 24” O.C. beams without modification to building structure, duct work and base unit. Condensate pan shall be internally sloped and conform to ASHRAE 62-89 self-draining standards, with 3/4” NPTI copper, ridged mount connection.

INDOOR (EVAPORATOR) FAN ASSEMBLY

Fan shall be direct drive design. Fan wheel shall be double-inlet type with forward-curved blades, dynamically balanced to operate smoothly throughout the entire range of operation. Airflow design shall be constant air volume. Bearings shall be sealed and permanently lubricated for longer life and no maintenance. Fan assembly shall be “Slip Track” (slide-out) design for easy removal and cleaning.

OUTDOOR (CONDENSER) FAN ASSEMBLY

The outdoor fan shall be of the direct-driven propeller type, discharge air vertically, have aluminum blades riveted to corrosion resistant steel spider bracket and shall be statically balanced for smooth operation. The outdoor fan motor shall be totally enclosed with permanently lubricated bearings and internally protected against overload conditions.

REFRIGERANT COMPONENTS

Compressors:

A.	Shall be fully hermetic type, direct drive, internally protected with internal high-pressure relief and over temperature protection. The hermetic motor shall be suction gas cooled and have a voltage range of + or - 10% of the unit nameplate voltage.

B.	Shall have internal isolation and sound muffling to minimize vibration and noise, and be externally isolated on a dedicated, independent mounting.

Coils:

A.	Evaporator and condenser coils shall have aluminum plate fins mechanically bonded to seamless internally enhanced copper tubes with all joints brazed.

B.	Evaporator coil shall be of the direct expansion, blow through design, while condenser coil shall be draw through design.

Refrigerant Circuit and Refrigerant Safety Components:

A.	Shall include independent fixed orifice expansion devices.

B.	Shall include filter/strainer to eliminate any foreign matter.

GAS HEATING

Heat exchanger and exhaust system shall be constructed of aluminized steel and shall be designed with induced draft combustion with post purge logic and redundant main gas valve. The heat exchanger shall be of the tubular type, constructed of T1-40 aluminized steel for corrosion resistance and allowing minimum mixed air entering temperature of 40 ºF. Burners shall be of the in-shot type, constructed of aluminum-coated steel. All gas piping shall enter the unit cabinet at a single location through either the side or bottom, without any field modifications. An integrated control board shall provide timed control of evaporator fan functioning and burner ignition. Heating section shall be provided with the following minimum protection:

A.	Primary and auxiliary high-temperature limit switches.

B.	Induced draft pressure sensor.

C.	Flame roll out switch (manual reset).

D.	Flame proving controls.

UNIT OPERATING CHARACTERISTICS

Unit shall be capable of starting and running at 125º F outdoor temperature, exceeding maximum load criteria ARI Standard 210/240. The compressor, with standard controls, shall be capable of operation down to 45º F outdoor temperature. Accessory low ambient kit shall be available for operation to 0º F.

ELECTRICAL REQUIREMENTS

All unit power wiring shall enter unit cabinet at a single factory provided location and be capable of side or bottom entry, to minimize roof penetrations and avoid unit field modifications. Separate side and bottom openings shall be provided for the control wiring.

SPECIAL FEATURES

1.	Direct Digital Controls:

a.	Simplicity communicating controller shall be available as a factory-installed option.

2.	Micrometal 2” Spring Isolation Roof Curbs:

a.	Formed galvanized steel with wood nailer strip and capable of supporting entire unit weight.

b.	Allows for installing and securing ductwork to curb prior to mounting unit on the curb.

3.	Micrometal gear driven Integrated Economizers:

a.	Integrated integral-modulating type capable of simultaneous economizer and compressor operation.

b.	Includes all hardware and controls to provide cooling with outdoor air.

c.	Equipped with low-leakage dampers not to exceed 3% leakage, at 1 in. wg pressure differential (variable sliding economizer).

d.	Capable of introducing up to 100% outdoor air in both minimum and fully-open positions. Equipped with a gravity relief sliding plate damper (variable sliding economizer). Damper shall close upon unit shutoff.

4.	UVC lights from Steril-Aire.

Provide and install UVC EMITTERS of the type and size necessary to provide the following and install only in accordance with the manufacturers recommendations. To continuously kill surface and airborne microorganisms, supply and install significant quantities of UVC EMITTERS downstream of each cooling coil such that a minimum of 1000 uW/cm2 strikes the coil fins at the closest point and through placement, not less than 60% of that value at the farthest point.  Equal amounts are to strike the drain pan, either directly or indirectly through reflection.