# YORK® MECHANICAL SPECIFICATIONS

SINGLE PACKAGE GAS/ELECTRIC ROOFTOP UNITS

6-1/2 THRU 12-1/2 NOMINAL TONS

PREDATOR® SERIES

Size Range:	6-1/2 to 12-1/2 Tons Nominal Cooling

100,000 to 200,000 BTUH Nominal Gas Heating Output

Model Series: ZH

# GENERAL

Units shall be manufactured by York International Unitary Products Group in an ISO 9001 certified facility. YORK® Predator® units are convertible single packages with a common footprint cabinet and common roof curb for all 6-1/2 through 12-1/2 ton models. All units have two compressors with independent refrigeration circuits to provide 2 stages of cooling. The units were designed for light commercial applications and can be easily installed on a roof curb, slab, or frame. All Predator® units are self-contained and assembled on rigid full perimeter base rails allowing for 3-way forklift access and overhead rigging. Every unit is completely charged, wired, piped, and tested at the factory to provide a quick and easy field installation. All units are convertible between side and down airflow. Independent economizer designs are used on side and down discharge applications, as well as all tonnage sizes.

# DESCRIPTION

Units shall be factory assembled, R410A single package, designed for outdoor installation. They shall have built in field convertible duct connections for down discharge supply/return or horizontal discharge supply/return and be available with factory installed options or field installed accessories. The units shall be factory wired, piped, charged, and factory tested prior to shipment. All unit wiring shall be both numbered and color coded. The cooling performance shall be rated in accordance with DOE and ARI test procedures. Units shall be CSA certified to ANSI Z21.47 and UL 1995/CAN/CSA No. 236-M90 standards.

# UNIT CABINET

Unit cabinet shall be constructed of G90 galvanized steel with exterior surfaces coated with a non-chalking, powder paint finish, certified at 1000 hour salt spray test per ASTM-B117 standards. Indoor blower sections shall be insulated with up to 1” thick insulation coated on the airside. Aluminum foil faced insulation shall be used in the unit’s compartments and be fastened to prevent insulation from entering the air stream. Cabinet doors shall be hinged with toolless access for easy servicing and maintenance. Full perimeter base rails shall be provided to assure reliable transit of equipment, overhead rigging, fork truck access and proper sealing on roof curb applications. Disposable 2” filters shall be furnished and be accessible through hinged access door. Fan performance measuring ports shall be provided on the outside of the cabinet to allow accurate air measurements of evaporator fan performance without removing panels or creating bypass of the coils. Condensate pan shall be slide out design, constructed of a non corrosive material, internally sloped and conforming to ASHRAE 62-89 standards. Condensate connection shall be a minimum of ¾” I.D. female and be rigid mount connection.

# INDOOR (EVAPORATOR) FAN ASSEMBLY

Fan shall be a belt drive assembly and include an adjustable pitch motor pulley. Job site selected brake horsepower shall not exceed the motors nameplate horsepower rating plus the service factor. Units shall be designed to operate within the service factor. Fan wheel shall be double inlet type with forward curve blades, dynamically balanced to operate smoothly throughout the entire range of operation. Airflow design shall be constant volume. Bearings shall be sealed and permanently lubricated for longer life and no maintenance. Entire blower assembly and motor shall be slide out design.

# OUTDOOR (CONDENSER) FAN ASSEMBLY

The outdoor fans shall be of the direct drive type, discharge air vertically, have aluminum blades riveted to corrosion resistant steel spider brackets and shall be dynamically balanced for smooth operation. The outdoor fan motors shall have permanently lubricated bearings internally protected against overload conditions and staged independently. A cleaning window shall be provided on two sides of the units for coil cleaning.

# REFRIGERANT COMPONENTS

Compressors:

- Shall be fully hermetic type, direct drive, internally protected with internal high-pressure relief and over temperature protection. The hermetic motor shall be suction gas cooled and have a voltage range of + or – 10% of the unit nameplate voltage.

- Shall have internal spring isolation and sound muffling to minimize vibration and noise, and be externally isolated on a dedicated, independent mounting.

Coils:

- Evaporator and Condenser coils shall have aluminum plate fins mechanically bonded to seamless internally enhanced copper tubes with all joints brazed. Special Phenolic coating shall be available as a factory option.

- Evaporator and Condenser coils shall be of the direct expansion, draw-thru design.

Refrigerant Circuit and Refrigerant Safety Components:

  - Independent fixed-orifice or thermally operated expansion devices.

  - Solid core filter drier/strainer to eliminate any moisture or foreign matter.

  - Accessible service gage connections on both suction and liquid lines to charge, evacuate, and measure refrigerant pressure during any necessary servicing or troubleshooting, without losing charge.

  - The unit shall have two independent refrigerant circuits, equally split in 50% capacity increments.

# UNIT CONTROLS

- Unit shall be complete with self-contained low-voltage control circuit protected by a resettable circuit breaker on the 24-volt transformer side.

- Unit shall incorporate a lockout circuit which provides reset capability at the space thermostat or base unit should any of the following standard safety devices trip and shut off compressor:

- Loss-of-charge/Low-pressure switch.

- High-pressure switch.

- Freeze-protection thermostat, evaporator coil. If any of the above safety devices trip, an LED (light-emitting diode) indicator shall flash a diagnostic code that indicates which safety switch has tripped.

- Unit shall incorporate “AUTO RESET” compressor over temperature, over current protection.

- Unit shall operate with conventional thermostat designs and have a low voltage terminal strip for easy hook-up.

- Unit control board shall have on-board diagnostics and fault code display.

- Standard controls shall include anti-short cycle and low voltage protection, and permit cooling operation down to 0 ºF.

- Control board shall monitor each refrigerant safety switch independently.

- Control board shall retain last 5 fault codes in non-volatile memory, which will not be lost in the event of a power loss.

# GAS HEATING SECTION

Heat exchanger and exhaust system shall be constructed of aluminized steel and shall be designed with induced draft combustion with post purge logic, energy saving direct spark ignition, and redundant main gas valve. The heat exchanger shall be of the tubular type, constructed of T1-40 aluminized steel for corrosion resistance and allowing minimum mixed air entering temperature of 40 ºF. Burners shall be of the in-shot type, constructed of aluminum-coated steel. All gas piping shall enter the unit cabinet at a single location, through either the side or bottom, without any field modifications. An integrated control board shall provide timed control of evaporator fan functioning and burner ignition. Heating section shall be provided with the following minimum protection:

- Primary and auxiliary high-temperature limit switches.

- Induced draft motor speed sensor.

- Flame roll out switch.

- Flame proving controls.

- Flame proving controls. Unit shall have two independent stages of capacity (60% 1st stage, 100% 2nd stage).

# UNIT OPERATING CHARACTERISTICS

Unit shall be capable of starting and running at 125 ºF outdoor temperature, exceeding maximum load criteria of ARI Standard 340/360. The compressor, with standard controls, shall be capable of operation down to 0 ºF outdoor temperature. Unit shall be provided with fan time delay to prevent cold air delivery before heat exchanger warms up. (Gas heat only)

# ELECTRICAL REQUIREMENTS

All unit power wiring shall enter unit cabinet at a single factory provided location and be capable of side or bottom entry to minimize roof penetrations and avoid unit field modifications. Separate side and bottom openings shall be provided for the control wiring.

# SPECIAL FEATURES

1.	Direct Digital Controls:

a.	Simplicity communicating controller shall be available as a factory-installed option.

2.	2” Spring fully welded IBC Calculated Isolation Roof Curbs:

a.	Formed galvanized steel with wood nailer strip and capable of supporting entire unit weight.

b.	Allows for installing and securing ductwork to curb prior to mounting unit on the curb.

3.	Gear driven Integrated Economizers:

a.	Integrated integral-modulating type capable of simultaneous economizer and compressor operation.

b.	Includes all hardware and controls to provide cooling with outdoor air.

c.	Equipped with low-leakage dampers not to exceed 3% leakage, at 1 in. wg pressure differential (variable sliding economizer).

d.	Capable of introducing up to 100% outdoor air in both minimum and fully-open positions. Equipped with a gravity relief sliding plate damper (variable sliding economizer). Damper shall close upon unit shutoff.

4.	UVC lights from Steril-Aire.

Provide and install UVC EMITTERS of the type and size necessary to provide the following and install only in accordance with the manufacturers recommendations. To continuously kill surface and airborne microorganisms, supply and install significant quantities of UVC EMITTERS downstream of each cooling coil such that a minimum of 1000 uW/cm2 strikes the coil fins at the closest point and through placement, not less than 60% of that value at the farthest point.  Equal amounts are to strike the drain pan, either directly or indirectly through reflection.

5.	Modulating Centrifugal Power Exhaust Controlled by pressure in the space.

Provide and install for each unit a modulating centrifugal power exhaust to control a neutral pressure in the space. Pressure sensor shall be installed in the space.

6.	ArmorGuard SS316 Coils and Casing Coating:

Condenser and Evaporator coils must be treated with ArmorGuard SS316, water reducible, liquid stainless steel hard acrylic emulsion corrosion protection coating with 316 stainless steel flake. Coating must be non flammable, non hazardous, environmentally safe, super low VOC, and offer high corrosion protection with superior adhesion and proven long term durability. Coating to be UV resistant and USDA approved.

7.	Provide Slide Out Fan Chassis

8.	Stainless Steel Drain Pan

9.	Stainless Steel on Entire Heat Exchanger

10.	Hinged Filter with Filter Switch and Tooless Access Panels

11.	2” Pleated Filters

12.	Phase Protection (loss, imbalance and reversal)

13.	T2950 365 Days Thermostat

14.	CO2 Demand Control Ventilation,

15.	Freeze and Under voltage Protections, High/Low Pressure switch

16.	Smoke Detectors in both Supply and Return