# YORK® MECHANICAL SPECIFICATIONS

SINGLE PACKAGE GAS HEATING/ELECTRIC COOLING

3 THRU 6 NOMINAL TONS

SUNLINE™ SERIES

Size Range:	3 to 5 Tons Nominal Cooling

40,000 to 100, 000 BTUH Nominal Gas Heating Output

Model Series:	ZJ

# GENERAL

These units are convertible single package units. Although the units are primarily designed for curb mounting on a roof, they can also be slab-mounted at ground level or set on steel beams above a finished roof. Cooling with gas heat are available with a wide variety of factory-mounted options and field-installed accessories to make them suitable for almost every application. All units are self-contained and assembled on full perimeter base rails with holes in the four corners for overhead rigging. Every unit is completely piped, wired, charged and tested at the factory to simplify the field installation and to provide years of dependable operation. All models (including those with an economizer) are suitable for either bottom or horizontal duct connections. Models with power exhaust are suitable for bottom duct connections only. For bottom duct, remove the sheet metal panels from the supply and return air openings through the base of the unit. For horizontal duct, remove the supply and return air panels on the rear of the unit.

All non-Scroll compressors include crankcase heaters and all compressors have internal pressure relief. Every refrigerant circuit includes a liquid line filter-drier, a discharge line high pressure switch and a suction line with a freezestat and low pressure/loss of charge switch. The unit control circuit includes a 75 VA transformer, a 24-volt circuit breaker and a relay board with a compressor lockout circuit, a terminal strip for thermostat wiring, plus an additional set of pin connectors to simplify the interface of additional field controls. All models are CSA listed. All models include a 1-year limited warranty on the complete unit. Compressors and electric heater elements carry a 5-year warranty. Aluminized steel and Stainless steel tubular heat exchangers carry a 10-year warranty.

# DESCRIPTION

Units shall be factory-assembled, single packaged, Electric Cooling/Gas Heat are designed for outdoor mounted installation.

They shall have built-in field convertible duct connections for down discharge supply/return or horizontal discharge supply/return, and be available with factory installed options or field installed accessories. The units shall be factory wired, piped, charged with R-410A refrigerant and factory tested prior to shipment. All unit wiring shall be both numbered and color coded. All units the cooling performance shall be rated in accordance with DOE and ARI test procedures. Units shall be CSA listed, classified to ANSI Z21.47, UL 1995/CSA No. 236 standards.

# UNIT CABINET

Unit cabinet shall be constructed of G90 galvanized steel, with exterior surfaces coated with a non-chalking, powdered paint finish, certified at 1000 hours salt spray test per ASTMB117 standards. Indoor blower section shall be insulated with a minimum 1/2” thick insulation, coated on the airside. Aluminum foil faced insulation shall be used in the furnace compartment and be fastened with ridged fasteners to prevent insulation from entering the air stream. Cabinet panels shall be “large” size, easily removable for servicing and maintenance. Full perimeter base rails shall be provided to assure reliable transit of equipment, overhead rigging and proper sealing on roof curb applications. Disposable 1" filters shall be furnished and be accessible through a removable access door, sealed airtight. Units filter track shall be designed to accommodate either 1" or 2" filters. Fan performance measuring ports shall be provided on the outside of the cabinet to allow accurate air measurements of evaporator fan performance without removing panels or creating air by-pass of the coils. Condensate pan shall be internally sloped and conform to ASHRAE 62-89 self-draining standards. Condensate connection shall be a minimum of 3/4” I.D. female and be a ridged mount connection.

# INDOOR (EVAPORATOR) FAN ASSEMBLY

The indoor fan shall be a factory installed belt drive assembly that includes an adjustable pitch motor pulley. Job site selected (B.H.P.) brake horsepower shall not exceed the motors nameplate horsepower rating, plus the service factor. Units shall be designed not to operate above service factor. Fan wheel shall be double-inlet type with forward-curved blades, dynamically balanced to operate smoothly throughout the entire range of operation. Airflow design shall be constant air volume. Bearings shall be sealed and permanently lubricated for longer life and no maintenance.

# OUTDOOR (CONDENSER) FAN ASSEMBLY

The indoor fan shall be a factory installed belt drive assembly that includes an adjustable pitch motor pulley. Job site selected (B.H.P.) brake horsepower shall not exceed the motors nameplate horsepower rating, plus the service factor. Units shall be designed not to operate above service factor. Fan wheel shall be double-inlet type with forward-curved blades, dynamically balanced to operate smoothly throughout the entire range of operation. Airflow design shall be constant air volume. Bearings shall be sealed and permanently lubricated for longer life and no maintenance.

# REFRIGERANT COMPONENTS

Compressors:

- Shall be internally protected with internal high-pressure relief and over temperature protection.

- Shall have internal spring isolation and sound muffling to minimize vibration and noise, and be externally isolated on a dedicated, independent mounting.

Coils:

- Evaporator and Condenser coils shall have aluminum plate fins mechanically bonded to seamless internally enhanced copper tubes with all joints brazed. Special Phenolic coating shall be available as a factory option.

- Evaporator and Condenser coils shall be of the direct expansion, draw-thru design.

Refrigerant Circuit and Refrigerant Safety Components:

  - Independent fixed-orifice or thermally operated expansion devices.

  - Filter drier/strainer to eliminate any moisture or foreign matter.

  - Accessible service gage connections on both suction and liquid lines to charge, evacuate, and measure refrigerant pressure during any necessary servicing or troubleshooting, without losing charge.

  - The refrigeration system shall provide at least 15°F of sub-cooling at design conditions.

  - Heat pump models shall include factory mounted reversing valve and suction line accumulator.

# UNIT CONTROLS

- Unit shall be complete with self-contained low-voltage control circuit protected by a resettable circuit breaker on the 24-volt transformer side.

- Unit shall incorporate a lockout circuit which provides reset capability at the space thermostat or base unit, should any of the following standard safety devices trip and shut off compressor.

- Loss-of-charge/Low-pressure switch.

- High-pressure switch.

- Freeze-protection thermostat, evaporator coil.

- Unit shall incorporate “AUTO RESET” compressor over temperature, over current protection.

- Unit shall operate with conventional thermostat designs and have a low voltage terminal strip for easy hook-up.

- Unit control board shall have on-board diagnostics and fault code display.

- Standard controls shall include anti-short cycle and low voltage protection, and permit cooling operation down to 0°F.

- Control board shall monitor each refrigerant safety switch independently.

- Control board shall retain last 5 fault codes in non volatile memory which will not be lost in the event of a power loss.

# GAS HEATING SECTION (SINGLE OR 2 STAGE)

Shall be designed with induced draft combustion with post purge logic, energy saving direct spark ignition, and redundant main gas valve. Venter wheel shall be constructed of stainless steel for corrosion resistance. The heat exchanger shall be of the tubular type, constructed of T1-40 aluminized steel for corrosion resistance and allowing minimum mixed air entering temperature of 25°F. Burners shall be of the in-shot type, constructed of aluminum coated steel and contain air mixture adjustments. All gas piping shall enter the unit cabinet at a single location through either the side or curb without any field modifications. Integrated control boards shall provide timed control of evaporator fan functioning and burner ignition. Heating section shall be provided with the following minimum protection:

- Primary and auxiliary high-temperature limit switches.

- Induced draft motor speed sensor.

- Flame roll out switch.

- Flame proving controls.

- If any of the above safety devices trip, a LED (light-emitting diode) indicator shall flash a diagnostic code that indicates which safety switch has tripped.

# UNIT OPERATING CHARACTERISTICS

Unit shall be capable of starting and running at 125°F outdoor temperature, exceeding maximum load criteria of ARI Standard 210/240. The compressor, with standard controls, shall be capable of operation down to 0°F outdoor temperature. Unit shall be provided with fan time delay to prevent cold air delivery before heat exchanger warms up (Gas heat only).

# ELECTRICAL REQUIREMENTS

All unit power wiring shall enter unit cabinet at a single factory provided location and be capable of side or bottom entry, to minimize roof penetrations and avoid unit field modifications. Separate side and bottom openings shall be provided for the control wiring.

# SPECIAL FEATURES

1.	Direct Digital Controls:

a.	Simplicity communicating controller shall be available as a factory-installed option.

2.	2” Spring fully welded IBC Calculated Isolation Roof Curbs:

a.	Formed galvanized steel with wood nailer strip and capable of supporting entire unit weight.

b.	Allows for installing and securing ductwork to curb prior to mounting unit on the curb.

3.	Gear driven Integrated Economizers:

a.	Integrated integral-modulating type capable of simultaneous economizer and compressor operation.

b.	Includes all hardware and controls to provide cooling with outdoor air.

c.	Equipped with low-leakage dampers not to exceed 3% leakage, at 1 in. wg pressure differential (variable sliding economizer).

d.	Capable of introducing up to 100% outdoor air in both minimum and fully-open positions. Equipped with a gravity relief sliding plate damper (variable sliding economizer). Damper shall close upon unit shutoff.

4.	UVC lights from Steril-Aire.

Provide and install UVC EMITTERS of the type and size necessary to provide the following and install only in accordance with the manufacturers recommendations. To continuously kill surface and airborne microorganisms, supply and install significant quantities of UVC EMITTERS downstream of each cooling coil such that a minimum of 1000 uW/cm2 strikes the coil fins at the closest point and through placement, not less than 60% of that value at the farthest point.  Equal amounts are to strike the drain pan, either directly or indirectly through reflection.

5.	Modulating Centrifugal Power Exhaust Controlled by pressure in the space.

Provide and install for each unit a modulating centrifugal power exhaust to control a neutral pressure in the space. Pressure sensor shall be installed in the space.

6.	ArmorGuard SS316 Coils and Casing Coating:

Condenser and Evaporator coils must be treated with ArmorGuard SS316, water reducible, liquid stainless steel hard acrylic emulsion corrosion protection coating with 316 stainless steel flake. Coating must be non flammable, non hazardous, environmentally safe, super low VOC, and offer high corrosion protection with superior adhesion and proven long term durability. Coating to be UV resistant and USDA approved.

7.	Provide Slide Out Fan Chassis

8.	Stainless Steel Drain Pan

9.	Stainless Steel on Entire Heat Exchanger

10.	Hinged Filter with Filter Switch and Tooless Access Panels

11.	2” Pleated Filters

12.	Phase Protection (loss, imbalance and reversal)

13.	T2950 365 Days Thermostat

14.	CO2 Demand Control Ventilation,

15.	Freeze and Under voltage Protections, High/Low Pressure switch

16.	Smoke Detectors in both Supply and Return